## Cover
General Rate Case TY 2024
(SDG&E-Risk-1-QWP)
Wildfire
Workpapers
May 2022

## RSE Summary WF Supplemental
Control/Mitigation Name | GeneratorGrantPrograms |  | Control/Mitigation Name | CoveredConductors |  | Control/Mitigation Name | Strategic_Undergrounding
PSPS Risk Inputs | Resiliency Grant Programs (HFTD Tier 3) | Resiliency Grant Programs (HFTD Tier 2) | Wildfire Risk Inputs | Wildfire Risk - Tier 3 | Wildfire Risk - Tier 2 | Wildfire Risk Inputs | Wildfire Risk - Tier 3 | Wildfire Risk - Tier 2
PSPS mitigation % effectiveness | 40% | 40% | Numbers of Average Veg Risk Event Prior Mitigation | 6.48 | 7.02 | Numbers of Average Risk Event Prior Mitigation (per 100miles) | 13.5 | 13.5
Pre-Mitigation LoRE | 1 | 0.5 | Historical Ignition Rate | 4.298% | 4.328% | Historical Ignition Rate | 4.298% | 4.328%
% Change in LoRE Reduction | 40% | 20% | Installation/Repairment/Replacement Year 1 |  |  | Installation/Repairment/Replacement Year 1
Projected 2024 Residential/Industrial/Commercial | 0 | 0 | Installation/Repairment/Replacement Year 2 |  |  | Installation/Repairment/Replacement Year 2 | 78.8 | 46.3
Projected 2024 Essential | 142.8571 | 666.6667 | Installation/Repairment/Replacement Year 3 | 82 | 18 | Installation/Repairment/Replacement Year 3
Projected 2024 Urgent | 0 | 0 | Total Units in the Network | 100 | 100 | Total Units in the Network | 100 | 100
Projected 2024 Medical Baseline | 857.1429 | 3047.619 | Effectiveness Estimate | 64.5% | 64.5% | Effectiveness Estimate | 98% | 98%
Pre-Mitigation CoRE | 424.0718 | 1893.9916 | Total Ignition Reduced | 0.1473 | 0.035276 | Total Ignition Reduced | 0.44808 | 0.26512
Total Risk Reduction | 169.6287 | 378.7983 | Pre-Mitigation LoRE | 6.2 | 5.8 | Pre-Mitigation LoRE | 6.2 | 5.8
O&M Cost ($K) Year 3 | 3465 | 6934 | % Change in LoRE Reduction | 2.376% | 0.6082% | % Change in LoRE Reduction | 7.227% | 4.571%
Capital Cost ($K) Year 3 | 0 | 0 | Pre-Mitigation CoRE | 1562.1691 | 955.122 | Pre-Mitigation CoRE | 1562.1691 | 955.122
Total Year 3 Cost ($K) | 3465 | 6934 | Total Risk Reduction | 230.1137 | 33.6929 | Total Wildfire Risk Reduction | 699.9708 | 253.2266
Lifetime Benefits (Years) | 10 | 10 | O&M Cost ($K) Year 3 | 1309 | 287 | PSPS Risk Inputs | Strategic Undergrounding (HFTD Tier 3) | Strategic Undergrounding (HFTD Tier 2)
Discounted Time (Years) | 8.5302 | 8.5302 | Capital Cost ($K) Year 3 | 130888 | 28731 | PSPS mitigation % effectiveness | 100% | 100%
RSE per Million | 417.5952 | 465.9975 | Total Cost ($K) | 132197 | 29018 | Pre-Mitigation LoRE | 3.2 | 2.4
|  |  | Lifetime Benefits (Years) | 40 | 40 | Projected 2022 Residential/Industrial/Commercial | 1293.7577 | 1110.846
|  |  | Discounted Time (Years) | 23.1148 | 23.1148 | Projected 2022 Essential | 115.2423 | 12.9634
|  |  | RSE per Million | 40.2356 | 26.8386 | Projected 2022 Urgent | 0 | 0
[6 empty] | Projected 2022 Medical Baseline | 0 | 0.19064
[6 empty] | Pre-Mitigation CoRE | 392.8782 | 128.1515
[6 empty] | Total PSPS Risk Reduction | 1257.2104 | 307.5636
[6 empty] | O&M Cost ($K) Year 3 | 2592 | 1523
[6 empty] | Capital Cost ($K) Year 3 | 259246 | 152256
[6 empty] | Total Cost ($K) | 261838 | 153779
[6 empty] | Lifetime Benefits (Years) | 40 | 40
[6 empty] | Total Risk Reduction | 1957.1812 | 560.7903
[6 empty] | Discounted Time (Years) | 23.1148 | 23.1148
[6 empty] | RSE per Million | 172.7778 | 84.2933

## Risk Scoring Workpaper Summary
Risk Name | SDG&E Wildfire Involving SDG&E Equipment
Wildfire Risk - Tier 3 | LoRE | 6.2
| CoRE Safety | 569.9101
| CoRE Reliability | 89.0323
| CoRE Financial | 903.2267
| Total CoRE | 1562.1691
| Pre-Mitigated Risk Score | 9685.4482
Wildfire Risk - Tier 2 | LoRE | 5.8
| CoRE Safety | 348.0287
| CoRE Reliability | 55.5172
| CoRE Financial | 551.5761
| Total CoRE | 955.122
| Pre-Mitigated Risk Score | 5539.7075
Wildfire Risk - Non-HFTD | LoRE | 7.2
| CoRE Safety | 12.221
| CoRE Reliability | 2.875
| CoRE Financial | 19.3685
| Total CoRE | 34.4645
| Pre-Mitigated Risk Score | 248.1443
Wildfire Risk | LoRE | 19.2
| CoRE Safety | 293.75
| CoRE Reliability | 46.599
| CoRE Financial | 465.5521
| Total CoRE | 805.901
| Pre-Mitigated Risk Score | 15473.3
PSPS Risk - Tier 3 Standby Power Program | LoRE | 3.2 | PSPS Risk - Tier 2 Standby Power Program | LoRE | 2.4
| CoRE Safety | #REF! |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 Generator Grant Program | LoRE | 0.63172 | PSPS Risk - Tier 2 Generator Grant Program | LoRE | 0.12242
| CoRE Safety | 8.5001 |  | CoRE Safety | 31.4661
| CoRE Reliability | 827.4928 |  | CoRE Reliability | 3431.9693
| CoRE Financial | 40.1394 |  | CoRE Financial | 157.8766
| Total CoRE | 216.2766 |  | Total CoRE | 890.1761
| Pre-Mitigated Risk Score | 136.6254 |  | Pre-Mitigated Risk Score | 108.9785
PSPS Risk - Tier 3 Generator Assistance Program | LoRE | 0.63172 | PSPS Risk - Tier 2 Generator Assistance Program | LoRE | 0.12242
| CoRE Safety | #REF! |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 Resilience Program Microgrid | LoRE | 3.2 | PSPS Risk - Tier 2 Resilience Program Microgrid | LoRE | 2.4
| CoRE Safety | #REF! |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 PSPS Sectionalizing | LoRE | 3.2 | PSPS Risk - Tier 2 PSPS Sectionalizing | LoRE | 2.4
| CoRE Safety | #REF! |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  | Pre-Mitigated Risk Score | #REF!

## RiskSW_PSPS
Risk Name | SDG&E Wildfire Involving SDG&E Equipment
PSPS Risk - Tier 3 Standby Power Program | LoRE | 3.2 |  | PSPS Risk - Tier 2 Standby Power Program | LoRE | 2.4
| CoRE Safety | #REF! |  |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 Generator Grant Program | LoRE | 0.63172 |  | PSPS Risk - Tier 2 Generator Grant Program | LoRE | 0.12242
| CoRE Safety | 8.5001 |  |  | CoRE Safety | 31.4661
| CoRE Reliability | 827.4928 |  |  | CoRE Reliability | 3431.9693
| CoRE Financial | 40.1394 |  |  | CoRE Financial | 157.8766
| Total CoRE | 216.2766 |  |  | Total CoRE | 890.1761
| Pre-Mitigated Risk Score | 136.6254 |  |  | Pre-Mitigated Risk Score | 108.9785
PSPS Risk - Tier 3 Generator Assistance Program | LoRE | 0.63172 |  | PSPS Risk - Tier 2 Generator Assistance Program | LoRE | 0.12242
| CoRE Safety | #REF! |  |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 Resilience Program Microgrid | LoRE | 3.2 |  | PSPS Risk - Tier 2 Resilience Program Microgrid | LoRE | 2.4
| CoRE Safety | #REF! |  |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  |  | Pre-Mitigated Risk Score | #REF!
PSPS Risk - Tier 3 PSPS Sectionalizing | LoRE | 3.2 |  | PSPS Risk - Tier 2 PSPS Sectionalizing | LoRE | 2.4
| CoRE Safety | #REF! |  |  | CoRE Safety | #REF!
| CoRE Reliability | #REF! |  |  | CoRE Reliability | #REF!
| CoRE Financial | #REF! |  |  | CoRE Financial | #REF!
| Total CoRE | #REF! |  |  | Total CoRE | #REF!
| Pre-Mitigated Risk Score | #REF! |  |  | Pre-Mitigated Risk Score | #REF!
Name | Tier | Metric | Assumed Value | Source
System PSPS avg event per year | Tier 3 | LoRE | 3.2 | See Minal's screenshot
| Tier 2 | LoRE | 2.4 | See Minal's screenshot
| Tier 3 | Total Customers as 2021 | 29508
| Tier 2 | Total Customers as 2021 | 86224
| Tier 3 | Avg number of Customers affected per PSPS event | 5825.21 | calculated
| Tier 2 | Avg number of Customers affected per PSPS event | 4398.27 | calculated
| Tier 3 | ratio of avg PSPS customer divided by total customers | 19.74% | calculated
| Tier 2 | ratio of avg PSPS customer divided by total customers | 5.101% | calculated
Standby Power Program | Tier 3 | customer | #REF! | tab Standby Grant Program
| Tier 2 | customer | #REF! | tab Standby Grant Program
| Tier 3 | LoRE | 3.2 | These customers likely experience most PSPS events
| Tier 2 | LoRE | 2.4 | These customers likely experience most PSPS events
Generator Grant Program | Tier 3 | customer | 510 | tab Standby Grant Program
| Tier 2 | customer | 1745.7143 | tab Standby Grant Program
| Tier 3 | LoRE | 0.63172 | calculation
| Tier 2 | LoRE | 0.12242 | calculation
Generator Assistance Program | Tier 3 | customer | #REF! | tab Standby Grant Program
| Tier 2 | customer | #REF! | tab Standby Grant Program
| Tier 3 | LoRE | 0.63172
| Tier 2 | LoRE | 0.12242
Resilience Program Microgrids | Tier 3 | customer | #REF! | tab Standby Grant Program
| Tier 2 | customer | #REF! | tab Standby Grant Program
| Tier 3 | LoRE | 3.2
| Tier 2 | LoRE | 2.4
PSPS Sectionalizing | Tier 3 | customer | #REF! | tab Standby Grant Program
| Tier 2 | customer | #REF! | tab Standby Grant Program
| Tier 3 | LoRE | 3.2
| Tier 2 | LoRE | 2.4
[5 empty] | 2 | 4
Name | Incident Type | Metric | Assumed Value | Source
General Assumptions |  | avg number of ignitions in SDG&E territory | 15 | Internal data
|  | Expected total fire size | 200000 | SME Input, based on Wildfire Activity Statistics
|  | Total Significant Fire Incidents per Year | 0.05 | SME, internal data
|  | Total Serious Injuries and Fatalities (SIFs) per significant fire incident | 5.04 | SME, internal data
|  | % Tier 2 | 35.79% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | % Tier 3 | 62.65% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | % Non-HFTD | 1.56% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | Tier 2 -- avg acres per year | 238.6012
|  | Tier 3 -- avg acres per year | 417.6646
|  | non HFTD -- avg acres per year | 10.4008
|  | Total safety index per year | 0.752 | Calculation
|  | $ per acre | 1766
|  | $ per structure damaged | 1000000
|  | Structures per acre | 0.00875
Wildfire LoRE | Tier 3 | Total Incidents per Year | 6.2 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
| Tier 2 | Total Incidents per Year | 5.8 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
| Non-HFTD | Total incidents per year | 7.2 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
PSPS LoRE | Tier 3 and Tier 2 | Total incidents per year | 4 | Internal reliability data
Safety | HFTD
|  | % Tier 2 safety index of total safety index | 36.8% | SME Input
|  | % Tier 3 safety index of total safety index | 63.2% | SME Input
|  | Tier 2 Safety index per incident | 0.26914 | Calculation
|  | Tier 3 Safety index per incident | 0.47113 | Calculation
Non-HFTD
|  | Total Non-HFTD safety index per incident | 0.011732 | Calculation
| PSPS | Total safety incidents per year | 0.017772 | SME, internal data
|  | % Tier 3 safety index of total safety index | 70% | SME, internal data
|  | % Tier 2 safety index of total safety index | 30% | SME, internal data
|  | Tier 3 safety index per incident | 0.0031101 | Calculation
|  | Tier 2 safety index per incident | 0.0013329 | Calculation
Financial | HFTD
|  | Tier 3, $M USD per incident (repair cost, destruction of property) | 4.3922 | Calculation
|  | Tier 2, $M USD per incident (repair cost, destruction of property) | 2.5091 | Calculation
Non-HFTD
|  | $M USD per year (repair cost, destruction of property) | 3.8241e-06 | Calculation
| PSPS | Tier 3, $M USD per incident (repair cost, destruction of property) | 12.9156 | SME, internal data
|  | Tier 2, $M USD per incident (repair cost, destruction of property) | 5.5352 | SME, internal data
Reliability | HFTD | Reliability index per incident, tier 3 | 0.003871 | SME based on internal reliability data
|  | Reliability index per incident, tier 2 | 0.0024138 | SME based on internal reliability data
| Non-HFTD | Reliability index per incident | 0.000125 | SME based on internal reliability data
| PSPS | Tier 3, SAIDI Minutes per year | 37.618 | SME, internal data
|  | Tier 3, SAIFI Outages per year | 0.02359 | SME, internal data
|  | Tier 3, Reliability Index per incident | 0.024986 | Calculation
|  | Tier 2, SAIDI Minutes per year | 16.122 | SME, internal data
|  | Tier 2, SAIFI Outages per year | 0.01011 | SME, internal data
|  | Tier 2, Reliability Index per incident | 0.010708 | Calculation

## Risk Scoring Workpaper
Risk Name | SDG&E Wildfire Involving SDG&E Equipment
Wildfire Risk - Tier 3 | LoRE | 6.2
| CoRE Safety | 569.9101
| CoRE Reliability | 89.0323
| CoRE Financial | 903.2267
| Total CoRE | 1562.1691
| Pre-Mitigated Risk Score | 9685.4482
Wildfire Risk - Tier 2 | LoRE | 5.8
| CoRE Safety | 348.0287
| CoRE Reliability | 55.5172
| CoRE Financial | 551.5761
| Total CoRE | 955.122
| Pre-Mitigated Risk Score | 5539.7075
Wildfire Risk - Non-HFTD | LoRE | 7.2
| CoRE Safety | 12.221
| CoRE Reliability | 2.875
| CoRE Financial | 19.3685
| Total CoRE | 34.4645
| Pre-Mitigated Risk Score | 248.1443
Wildfire Risk | LoRE | 19.2
| CoRE Safety | 293.75
| CoRE Reliability | 46.599
| CoRE Financial | 465.5521
| Total CoRE | 805.901
| Pre-Mitigated Risk Score | 15473.3
PSPS Risk - Tier 3 | LoRE | 4
| CoRE Safety | 9.3303
| CoRE Reliability | 542.57
| CoRE Financial | 439.1295
| Total CoRE | 991.0298
| Pre-Mitigated Risk Score | 3964.1191
PSPS Risk - Tier 2 | LoRE | 4
| CoRE Safety | 3.9987
| CoRE Reliability | 246.2869
| CoRE Financial | 188.1984
| Total CoRE | 438.4839
| Pre-Mitigated Risk Score | 1753.9357
PSPS Risk | LoRE | 4
| CoRE Safety | 13.3289
| CoRE Reliability | 788.8569
| CoRE Financial | 627.3279
| Total CoRE | 1429.5137
| Pre-Mitigated Risk Score | 5718.0548
Total Risk Score | Pre-Mitigated Risk Score | 21191.3548
Name | Incident Type | Metric | Assumed Value | Source
|  | Expected total fire size | 500000 | SME Input, based on Wildfire Activity Statistics
|  | Total Significant Fire Incidents per Year | 0.05 | SME, internal data
|  | Total Serious Injuries and Fatalities (SIFs) per significant fire incident | 12.6 | SME, internal data
|  | % Tier 2 | 35.79% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | % Tier 3 | 62.65% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | % Non-HFTD | 1.56% | calculated from Technosylva simulations, ratios based on cAcrAve
|  | Tier 2 -- avg acres per year | 8947.5455
|  | Tier 3 -- avg acres per year | 15662.4234
|  | non HFTD -- avg acres per year | 390.0311
|  | Total safety index per year | 1.88 | Calculation
|  | $ per acre | 1766 | SME assumption
|  | $ per structure damaged | 1000000 | SME assumption
|  | Structures per acre | 0.00875 | SME assumption
Wildfire LoRE | Tier 3 | Total Incidents per Year | 6.2 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
| Tier 2 | Total Incidents per Year | 5.8 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
| Non-HFTD | Total incidents per year | 7.2 | See Masters Inputs -- 2017 –2021 ignition data, SME inputs
PSPS LoRE | Tier 3 and Tier 2 | Total incidents per year | 4 | Internal reliability data
Safety | HFTD
|  | % Tier 2 safety index of total safety index | 35.79% | SME Input
|  | % Tier 3 safety index of total safety index | 62.65% | SME Input
|  | Tier 2 Safety index per incident | 0.11601 | Calculation
|  | Tier 3 Safety index per incident | 0.18997 | Calculation
Non-HFTD
|  | Total Non-HFTD safety index per incident | 0.0040737 | Calculation
| PSPS | Total safety incidents per year | 0.017772 | SME, internal data
|  | % Tier 3 safety index of total safety index | 70% | SME, internal data
|  | % Tier 2 safety index of total safety index | 30% | SME, internal data
|  | Tier 3 safety index per incident | 0.0031101 | Calculation
|  | Tier 2 safety index per incident | 0.0013329 | Calculation
Financial | HFTD
|  | Tier 3, $M USD per incident (repair cost, destruction of property) | 26.5655 | Calculation | 26.5655
|  | Tier 2, $M USD per incident (repair cost, destruction of property) | 16.2228 | Calculation
Non-HFTD
|  | $M USD per year (repair cost, destruction of property) | 0.56966 | Calculation
| PSPS | Tier 3, $M USD per incident (repair cost, destruction of property) | 12.9156 | SME, internal data
|  | Tier 2, $M USD per incident (repair cost, destruction of property) | 5.5352 | SME, internal data
Reliability | HFTD | Reliability index per incident, tier 3 | 0.003871 | SME based on internal reliability data
|  | Reliability index per incident, tier 2 | 0.0024138 | SME based on internal reliability data
| Non-HFTD | Reliability index per incident | 0.000125 | SME based on internal reliability data
| PSPS | Tier 3, SAIDI Minutes per year | 37.618 | SME, internal data
|  | Tier 3, SAIFI Outages per year | 0.02359 | SME, internal data
|  | Tier 3, Reliability Index per incident | 0.024986 | Calculation
|  | Tier 2, SAIDI Minutes per year | 16.122 | SME, internal data
|  | Tier 2, SAIFI Outages per year | 0.01011 | SME, internal data
|  | Tier 2, Reliability Index per incident | 0.010708 | Calculation

## Master Inputs
Master Inputs
Discount Factors
Benefit Discount Factor | 3%
MAVF Framework
| Range | Weight | WeightD | Weightn
Safety Index | 20 | 60% | 0.6 | 60%
Reliability Index | 1 | 23% | 0.23 | 23%
Financial Cost | 500 | 15% | 0.15 | 17%
Stakeholder Satisfaction Index | 0 | 0% | 0
SAIDI | 100 | 25% | 0.25 | 0.25
SAIFI | 1 | 25% | 0.25 | 0.25
FinancialImpactPerCustomer | 250
ReadabilityFactor | 100000
LengthofPSPSShutdown | 1920
SafetyCustomerMinutes | 10000000000
TotalCustomersSDGE | 1491385
| CoRE | Safety | Reliability | Financial
MedicalFactors | 0.089261 | 0.00288 | 0.077881 | 0.0085 |  | 0.6
Residential | 0.086957 | 0.000576 | 0.077881 | 0.0085 |  | 20
Essential | 2.4329 | 0.01152 | 2.3364 | 0.085
| Risk Events | [6 empty] | Ignitions
Location | 2017 | 2018 | 2019 | 2020 | 2021 | 5-year Avg | 2017 | 2018 | 2019 | 2020 | 2021 | 5-year Avg | 2017-2021
[6 empty] | (2017-2021) | [5 empty] | (2017-2021)
Non-HFTD | 649 | 593 | 591 | 615 | 720 | 633.6 | 8 | 11 | 6 | 6 | 5 | 7.2 | 1.136%
Tier 2 | 231 | 182 | 235 | 220 | 269 | 227.4 | 6 | 5 | 7 | 6 | 5 | 5.8 | 2.551%
Tier 3 | 193 | 199 | 248 | 195 | 230 | 213 | 7 | 5 | 2 | 11 | 6 | 6.2 | 2.911%
System | 1073 | 974 | 1074 | 1030 | 1219 | 1074 | 21 | 21 | 15 | 23 | 16 | 19.2 | 1.788%
HFTD (Tier 2 + Tier 3) | 424 | 381 | 483 | 415 | 499 | 440.4 | 13 | 10 | 9 | 17 | 11 | 12 | 2.725%
|  | Distribution Historical Faults | [5 empty] | Distribution Historical Ignitions | [7 empty] | 5 year average Ignition Rate
| HFTD | 2017 | 2018 | 2019 | 2020 | 2021 | 5-yr avg (2017-2021) | 2017 | 2018 | 2019 | 2020 | 2021 | 5-yr avg ignition (2017-2021) |  |  | Location | Normal | Elevated | Extreme | ALL
All Contact | System | 400 | 358 | 368 | 365 | 408 | 379.8 | 15 | 14 | 5 | 7 | 8 | 10.25 |  |  | Non-HFTD | 0.8743% | 0% | 156.5% | 1.866%
Veg. contact- Distribution | Non-HFTD | 48 | 22 | 21 | 25 | 31 | 29.4 | 1 | 3 | 0 | 1 | 0 | 1 |  |  | Tier 2 | 3.888% | 0.9091% | 73.08% | 4.328%
| Tier 2 | 13 | 9 | 2 | 4 | 5 | 6.6 | 0 | 0 | 1 | 0 | 0 | 0.2 |  |  | Tier 3 | 4.419% | 0.4796% | 84.21% | 4.298%
| Tier 3 | 9 | 3 | 4 | 2 | 4 | 4.4 | 2 | 0 | 0 | 0 | 0 | 0.4 |  |  | System | 1.997% | 0.4035% | 104.4% | 2.879%
| System | 70 | 34 | 27 | 31 | 40 | 40.4 | 3 | 3 | 1 | 1 | 0 | 1.6 |  |  | HFTD (Tier 2 + Tier 3) | 4.147% | 0.7001% | 77.78% | 4.314%
Animal contact- Distribution | Non-HFTD | 30 | 27 | 36 | 40 | 41 | 34.8 | 1 | 0 | 0 | 0 | 0 | 0.2
| Tier 2 | 28 | 22 | 26 | 30 | 25 | 26.2 | 0 | 0 | 1 | 0 | 2 | 0.6
| Tier 3 | 19 | 25 | 27 | 25 | 20 | 23.2 | 0 | 1 | 0 | 2 | 1 | 0.8
| System | 77 | 74 | 89 | 95 | 86 | 84.2 | 1 | 1 | 1 | 2 | 3 | 1.6 |  |  | 2017 | 2018 | 2019 | 2020 | 2021 | AVG
Balloon contact- Distribution | Non-HFTD | 109 | 96 | 79 | 94 | 124 | 100.4 | 3 | 3 | 0 | 1 | 2 | 1.8 |  |  | 15 | 14 | 5 | 7 | 8 | 9.8
| Tier 2 | 8 | 8 | 7 | 14 | 10 | 9.4 | 1 | 2 | 0 | 1 | 1 | 1 |  |  | 4 | 6 | 8 | 16 | 7 | 8.2
| Tier 3 | 3 | 8 | 7 | 3 | 1 | 4.4 | 1 | 3 | 0 | 0 | 0 | 0.8 |  |  | 19 | 20 | 13 | 23 | 15 | 18
| System | 120 | 112 | 93 | 111 | 135 | 114.2 | 5 | 8 | 0 | 2 | 3 | 3.6
Vehicle contact- Distribution | Non-HFTD | 59 | 60 | 67 | 66 | 62 | 62.8 | 1 | 0 | 1 | 0 | 0 | 0.4
| Tier 2 | 24 | 26 | 23 | 27 | 39 | 27.8 | 2 | 1 | 2 | 1 | 0 | 1.2
| Tier 3 | 10 | 13 | 10 | 14 | 19 | 13.2 | 1 | 0 | 0 | 1 | 0 | 0.4
| System | 93 | 99 | 100 | 107 | 120 | 103.8 | 4 | 1 | 3 | 2 | 0 | 2
Other contact from object - Distribution | Non-HFTD | 30 | 28 | 32 | 14 | 14 | 23.6 | 0 | 1 | 0 | 0 | 0 | 0.2
| Tier 2 | 7 | 7 | 17 | 5 | 7 | 8.6 | 1 | 0 | 0 | 0 | 1 | 0.4
| Tier 3 | 3 | 4 | 10 | 2 | 6 | 5 | 1 | 0 | 0 | 0 | 1 | 0.4
| System | 40 | 39 | 59 | 21 | 27 | 37.2 | 2 | 1 | 0 | 0 | 2 | 1
All Equipment Failure | System | 349 | 352 | 425 | 359 |  | 371.25 | 4 | 6 | 8 | 16 | 7 | 8.2
Capacitor bank damage or failure- Distribution | Non-HFTD | 2 | 10 | 11 | 11 | 12 | 9.2 | 0 | 0 | 0 | 0 | 1 | 0.2
| Tier 2 | 1 | 0 | 1 | 0 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 1 | 0 | 0.2
| System | 3 | 11 | 12 | 11 | 15 | 10.4 | 0 | 0 | 0 | 1 | 1 | 0.4
Conductor damage or failure — Distribution | Non-HFTD | 40 | 30 | 21 | 14 | 32 | 27.4 | 0 | 0 | 0 | 0 | 1 | 0.2
| Tier 2 | 15 | 7 | 13 | 8 | 12 | 11 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 16 | 7 | 18 | 10 | 21 | 14.4 | 1 | 0 | 0 | 1 | 1 | 0.6
| System | 71 | 44 | 52 | 32 | 65 | 52.8 | 1 | 0 | 0 | 1 | 2 | 0.8
Fuse damage or failure - Distribution | Non-HFTD | 42 | 39 | 44 | 59 | 45 | 45.8 | 1 | 0 | 0 | 1 | 0 | 0.4
| Tier 2 | 8 | 8 | 12 | 12 | 10 | 10 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 7 | 8 | 10 | 11 | 6 | 8.4 | 0 | 0 | 1 | 0 | 0 | 0.2
| System | 57 | 55 | 66 | 82 | 61 | 64.2 | 1 | 0 | 1 | 1 | 0 | 0.6
Lightning arrestor damage or failure- Distribution | Non-HFTD | 14 | 14 | 16 | 14 | 24 | 16.4 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 5 | 3 | 8 | 5 | 8 | 5.8 | 0 | 0 | 0 | 2 | 0 | 0.4
| Tier 3 | 7 | 3 | 4 | 4 | 6 | 4.8 | 1 | 0 | 0 | 3 | 0 | 0.8
| System | 26 | 20 | 28 | 23 | 38 | 27 | 1 | 0 | 0 | 5 | 0 | 1.2
Switch damage or failure- Distribution | Non-HFTD | 7 | 15 | 12 | 17 | 11 | 12.4 | 0 | 0 | 0 | 1 | 0 | 0.2
| Tier 2 | 3 | 4 | 3 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 0.4
| Tier 3 | 0 | 0 | 0 | 0 | 1 | 0.2 | 0 | 0 | 0 | 0 | 1 | 0.2
| System | 10 | 19 | 15 | 17 | 12 | 14.6 | 0 | 1 | 1 | 1 | 1 | 0.8
Pole damage or failure - Distribution | Non-HFTD | 23 | 12 | 30 | 15 | 18 | 19.6 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 25 | 5 | 14 | 3 | 16 | 12.6 | 0 | 0 | 0 | 1 | 0 | 0.2
| Tier 3 | 14 | 6 | 24 | 13 | 15 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0
| System | 62 | 23 | 68 | 31 | 49 | 46.6 | 0 | 0 | 0 | 1 | 0 | 0.2
Insulator and brushing damage or failure - Distribution | Non-HFTD | 6 | 5 | 6 | 4 | 6 | 5.4 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 1 | 2 | 3 | 0 | 5 | 2.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 2 | 1 | 0 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
| System | 7 | 9 | 10 | 4 | 11 | 8.2 | 0 | 0 | 0 | 0 | 0 | 0
Crossarm damage or failure - Distribution | Non-HFTD | 12 | 21 | 19 | 15 | 29 | 19.2 | 0 | 0 | 1 | 0 | 0 | 0.2
| Tier 2 | 1 | 5 | 5 | 8 | 9 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 7 | 4 | 10 | 6 | 7 | 6.8 | 0 | 0 | 0 | 0 | 0 | 0
| System | 20 | 30 | 34 | 29 | 45 | 31.6 | 0 | 0 | 1 | 0 | 0 | 0.2
Voltage regulator / booster damage or failure - Distribution | Non-HFTD | 0 | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 1 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| System | 1 | 1 | 0 | 1 | 3 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
Recloser damage or failure - Distribution | Non-HFTD | 0 | 0 | 1 | 2 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 0 | 0 | 1 | 2 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
| System | 0 | 1 | 2 | 5 | 1 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0
Anchor / guy damage or failure - Distribution | Non-HFTD | 0 | 1 | 1 | 0 | 1 | 0.6 | 0 | 1 | 1 | 0 | 0 | 0.4
| Tier 2 | 1 | 1 | 0 | 1 | 1 | 0.8 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0.25
| System | 1 | 2 | 1 | 1 | 2 | 1.4 | 0 | 1 | 1 | 1 | 0 | 0.6
Sectionalizer damage or failure - Distribution | Non-HFTD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Connection device damage or failure - Distribution | Non-HFTD | 27 | 33 | 38 | 43 | 42 | 36.6 | 0 | 0 | 1 | 1 | 0 | 0.4
| Tier 2 | 5 | 12 | 11 | 10 | 16 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 8 | 9 | 17 | 11 | 14 | 11.8 | 0 | 0 | 0 | 2 | 2 | 0.8
| System | 40 | 54 | 66 | 64 | 72 | 59.2 | 0 | 0 | 1 | 3 | 2 | 1.2
Transformer damage or failure - Distribution | Non-HFTD | 25 | 30 | 26 | 27 | 36 | 28.8 | 0 | 0 | 0 | 0 | 1 | 0.2
| Tier 2 | 7 | 14 | 8 | 16 | 21 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 6 | 19 | 12 | 12 | 16 | 13 | 0 | 1 | 0 | 0 | 0 | 0.2
| System | 38 | 63 | 46 | 55 | 73 | 55 | 0 | 1 | 0 | 0 | 1 | 0.4
Other - Distribution | Non-HFTD | 0 | 7 | 6 | 3 | 30 | 9.2 | 0 | 2 | 1 | 1 | 0 | 0.8
| Tier 2 | 3 | 7 | 8 | 1 | 21 | 8 | 1 | 1 | 1 | 1 | 0 | 0.8
| Tier 3 | 10 | 6 | 11 | 0 | 25 | 10.4 | 0 | 0 | 1 | 0 | 0 | 0.2
| System | 13 | 20 | 25 | 4 | 76 | 27.6 | 1 | 3 | 3 | 2 | 0 | 1.8
All Other | System | 324 | 264 | 281 | 306 | 288 | 292.6 | 2 | 1 | 2 | 0 | 1 | 1.2
Wire-to-wire contact / contamination- Distribution | Non-HFTD | 4 | 1 | 1 | 1 | 0 | 1.4 | 0 | 1 | 1 | 0 | 0 | 0.4
| Tier 2 | 4 | 0 | 3 | 0 | 0 | 1.4 | 0 | 0 | 1 | 0 | 0 | 0.2
| Tier 3 | 0 | 1 | 0 | 1 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
| System | 8 | 2 | 4 | 2 | 0 | 3.2 | 0 | 1 | 2 | 0 | 0 | 0.6
Contamination - Distribution | Non-HFTD | 0 | 0 | 2 | 0 | 4 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 0 | 0 | 0 | 0 | 1 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| System | 0 | 0 | 2 | 0 | 5 | 1.4 | 0 | 0 | 0 | 0 | 0 | 0
Utility work / Operation | Non-HFTD | 2 | 2 | 3 | 11 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 2 | 4 | 2 | 7 | 3 | 3.6 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 1 | 3 | 4 | 12 | 8 | 5.6 | 0 | 0 | 0 | 0 | 0 | 0
| System | 5 | 9 | 9 | 30 | 18 | 14.2 | 0 | 0 | 0 | 0 | 0 | 0
Vandalism / Theft - Distribution | Non-HFTD | 0 | 2 | 0 | 1 | 4 | 1.4 | 1 | 0 | 0 | 0 | 0 | 0.2
| Tier 2 | 0 | 0 | 1 | 3 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0.2
| Tier 3 | 1 | 1 | 1 | 2 | 1 | 1.2 | 0 | 0 | 0 | 0 | 0 | 0
| System | 1 | 3 | 2 | 6 | 6 | 3.6 | 1 | 0 | 0 | 0 | 1 | 0.4
All Other- Distribution | Non-HFTD | 0 | 1 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 3 | 0 | 0 | 0 | 2 | 0 | 0.4 | 0 | 0 | 0 | 0 | 0 | 0
| System | 0 | 1 | 0 | 2 | 0 | 0.6 | 0 | 0 | 0 | 0 | 0 | 0
Unknown - Distribution | Non-HFTD | 169 | 136 | 119 | 139 | 147 | 142 | 0 | 0 | 0 | 0 | 0 | 0
| Tier 2 | 69 | 38 | 67 | 63 | 52 | 57.8 | 1 | 0 | 0 | 0 | 0 | 0.2
| Tier 3 | 72 | 75 | 78 | 64 | 60 | 69.8 | 0 | 0 | 0 | 0 | 0 | 0
| System | 310 | 249 | 264 | 266 | 259 | 269.6 | 1 | 0 | 0 | 0 | 0 | 0.2
Grand Total - All Faults & Ignitions | System | 1073 | 974 | 1074 | 1030 | 696 | 969.4 | 21 | 21 | 15 | 23 | 16 | 19.2
Distributuion Hardening Data
Risk events before hardening | 9.23
Risk events after hardening | 5.12
Extrapolated Before Hardening | 13.504
Extrapolated After Hardening | 7.4908
Effectiveness | 44.5
Other Special Work Procedures:
Personnel Work Procedures and Infrasturcutre Protection Teams |  | Normal FPI |  |  |  |  | Elevated FPI |  |  |  | Extreme FPI or RFW
|  | Normal Days | Non-HFTD | Tier 2 | Tier 3 | System | Elevated Days | Non-HFTD | Tier 2 | Tier 3 | HFTD | Extreme or RFW Days | Non-HFTD | Tier 2 | Tier 3 | HFTD
| 2015 | 253 | 3 | 0 | 2 | 5 | 108 | 1 | 0 | 1 | 1 | 4 | 0 | 0 | 0 | 0
| 2016 | 206 | 8 | 0 | 3 | 11 | 138 | 0 | 1 | 3 | 4 | 21 | 0 | 0 | 0 | 0
| 2017 | 173 | 3 | 1 | 1 | 5 | 169 | 0 | 2 | 0 | 2 | 23 | 1 | 0 | 0 | 0
| 2018 | 169 | 3 | 4 | 3 | 10 | 182 | 1 | 2 | 3 | 5 | 14 | 0 | 0 | 0 | 0
| 2019 | 216 | 7 | 2 | 5 | 14 | 137 | 1 | 2 | 4 | 6 | 12 | 0 | 0 | 0 | 0
| 5 yr avg | 203.4 | 4.8 | 1.4 | 2.8 | 9 | 146.8 | 0.6 | 1.4 | 2.2 | 3.6 | 14.8 | 0.2 | 0 | 0 | 0
| normalized |  | 8.6136 | 2.5123 | 5.0246 | 16.1504 |  | 0 | 3.4809 | 5.47 |  | 0 | 20.2778 | 0
|  | Days |  | Tier 2 | Tier 3 |  | Faults per day Tier 2 |  | Faults per day Tier 3 |  | Extreme or RFW Procedures
Normal + Elevated 5 year average |  | 350.2 |  | 2.8 | 5 |  | 0.0079954 |  | 0.014278 |  |  |  | Tier 2 | Tier 3
[11 empty] | Risk events avoided |  | 0.11833 | 0.21131
[11 empty] | ignition rate |  | 10.34% | 10%
[11 empty] | ign avoided |  | 0.012241 | 0.021131
Recloser Protocoal
Faults By Tier And Weather Condition
| Non-HFTD |  |  | Tier 2 |  |  | Tier 3 |  |  | All Faults
Year | Normal | Elevated | Extreme | Normal | Elevated | Extreme | Normal | Elevated | Extreme
2015 | 159 | 33 | 0 | 58 | 25 | 0 | 43 | 30 | 0 | 348
2016 | 216 | 22 | 1 | 80 | 20 | 3 | 55 | 28 | 0 | 425
2017 | 169 | 44 | 5 | 52 | 32 | 4 | 42 | 20 | 2 | 370
2018 | 144 | 39 | 9 | 37 | 30 | 5 | 43 | 36 | 2 | 345
2019 | 155 | 23 | 0 | 59 | 39 | 2 | 45 | 43 | 1 | 367
avg | 168.6 | 32.2 | 3 | 57.2 | 29.2 | 2.8 | 45.6 | 31.4 | 1 | 371
5 yr avg. Ignition Rate
|  | Tier 2 |  |  | Tier 3
|  | Normal | Elevated | Extreme | Normal | Elevated | Extreme
|  | 2.17% | 5.06% | 10.34% | 1.6% | 4.35% | 10%
| Estimated Faults Avoided | [5 empty] | Estimated Ignition Avoided
| Tier 2 |  |  | Tier 3 |  |  | Tier 2 | Tier 3 | Total
Year | Normal | Elevated | Extreme | Normal | Elevated | Extreme
2016 |  | 50 | 0 |  | 60 | 0 | 2.53 | 2.61 | 5.14
2017 |  | 40 | 6 |  | 56 | 0 | 2.6444 | 2.436 | 5.0804
2018 | 104 | 64 | 8 | 86 | 40 | 4 | 6.3224 | 3.516 | 9.8384
2019 | 74 | 60 | 10 | 110 | 72 | 4 | 5.6758 | 5.292 | 10.9678
2020 | 118 | 78 | 4 | 84 | 86 | 2 | 6.921 | 5.285 | 12.206
5 yr Avg | 98.6667 | 58.4 | 5.6 | 93.3333 | 62.8 | 2 | 4.8187 | 3.8278 | 8.6465

## Inspection_Master_Inputs
WMP Inspection Analysis - Last Updated 01/26/2021
% Fail assumption |  |  | Ignition Rates - 5yr average (2017-2021) | [5 empty] | Ignition Counts - 5yr average (2017-2021)
40.8% | Emergency (0-3 days) |  | 2.91% | Distribution - HFTD Tier 3 |  | 2.78% | Transmission - HFTD Tier 3 |  | 6.2 | Distribution - HFTD Tier 3 |  | 0.5 | Transmission - HFTD Tier 3
4.08% | Priority (4-30 days) |  | 2.55% | Distribution - HFTD Tier 2 |  | 12.5% | Transmission - HFTD Tier 2 |  | 5.8 | Distribution - HFTD Tier 2 |  | 1.5 | Transmission - HFTD Tier 2
0.34% | Non-critical / Non-priority (6-12mos) |  | 1.14% | Distribution - Non-HFTD |  | 2.78% | Transmission - Non-HFTD |  | 9.2 | Distribution - Non-HFTD |  | 0.75 | Transmission - Non-HFTD
|  |  | 1.79% | Distribution - HFTD All |  | 9.24% | Transmission - HFTD All |  | 12 | Distribution - HFTD All |  | 2 | Transmission - HFTD All
|  |  | 2.095% | Distribution - System wide |  | 5.7% | Transmission - System wide |  | 21.2 | Distribution - System wide |  | 2.75 | Transmission - System wide
[6 empty] | 0% | Substation - System wide |  |  |  |  | 0 | Substation - system wide
Program |  |  | Overhead Detailed Inspections | Annual Patrol Inspections | Wood Pole Intrusive Inspections | HFTD Tier 3 Inspections (QA/QC) | Distribution Infrared Inspections | Distribution Drone Assessments | Circuit Ownership | Transmission Visual Inspections (patrol) | Transmission Detailed Inspections (ground) | Transmission Infrared Inspections | Additional Transmission Aerial 69kV Tier 3 Visual Inspections | Transmission Drone Assessments
Status |  |  | Established | Established | Established | Established | Pilot | Pilot | Completed, Done | Established | Established | Established | Established
RAMP classification |  |  | Control | Control | Control | Control | Mitigation | Mitigation | Mitigation | Control | Control | Control | Control
System |  |  | Distribution | Distribution | Distribution | Distribution | Distribution | Distribution | Distribution | Transmission | Transmission | Transmission | Transmission
Inspection Location |  |  | System | HFTD All | HFTD All | Tier 3 | HFTD All | HFTD All | System wide | System wide | System wide | System wide | Tier 3
Cycle |  |  | 5 | 1 | 10 | 3 | 5 | 5 | NA | 3 | 1 | 1 | 1
Summary Findings
4yr Forecast Total Ignitions Avoided - Tier 3 |  |  | 0.94666 | 0.90373 | 0.053526 | 0.94957 | 0 | 0.40684 | 0.0004947 | 0.023818 | 0.23042 | 0.072248 | 0.016643 | 0.027646
4yr Forecast Total Ignitions Avoided - Tier 2 |  |  | 0.6221 | 0.93249 | 0.035989 | 0 | 0.7716 | 1.407 | 0 | 0.040449 | 0.57301 | 0.15128 | 0 | 0.029531
4yr Forecast Total Ignitions Avoided - Non-HFTD |  |  | 1.211 | 1.284 | 0.56243 | 0.00086992 | 0 | 0.029023 | 0 | 0.023413 | 0.33684 | 0.077012 | 0 | 0.0080342
4yr Forecast Total Ignitions Avoided - HFTD All |  |  | 1.5688 | 1.8362 | 0.089515 | 0.94957 | 0.7716 | 1.8139 | 0.0004947 | 0.064267 | 0.80343 | 0.22352 | 0.016643 | 0.057177
4yr Forecast Total Ignitions Avoided - System |  |  | 2.7797 | 3.1202 | 0.65194 | 0.95044 | 0.7716 | 1.8429 | 0.0004947 | 0.087679 | 1.1403 | 0.30054 | 0.016643 | 0.065211
Historical Annual Faults Avoided |  |  | 48.4112 | 57.135 | 18.1716 | 10.7658 | 2 | 27.6692 | 0.0051 | 0.493 | 4.5628 | 0.02856 | 0.06528 | #DIV/0!
Historical Annual Ignitions Avoided |  |  | 1.0142 | 1.0227 | 0.32527 | 0.31328 | 0.0582 | 0.80517 | 0.00010684 | 0.045553 | 0.4216 | 0.0026389 | 0.0060319 | #DIV/0!
% of Avg Annual Ignitions Avoided |  |  | 8.452% | 8.523% | 2.711% | 5.053% | 0.485% | 6.71% | 0.000504% | 1.656% | 15.33% | 0.09596% | 0.2193% | #DIV/0!
Hit Rates | System | Emergency (0-3 days) | 0.0020032 | 0.00053958 | 0.0015088 | 0.0013086 | 0 | 0.0033598 | 0 | 0 | 0.00017917 | 0 | 0 | #DIV/0!
|  | Priority (4-30 days) | 0.00073871 | 0.00049965 | 0.0013093 | 0.0052655 | 0.00015294 | 0.055101 | 0 | 0.00071751 | 0.011789 | 4.1815e-05 | 0.00084282 | #DIV/0!
|  | Non-critical | 0.06011 | 0.0038214 | 0.034953 | 0.026421 | 0 | 0.24534 | 1 | 0.00084797 | 0.077472 | 8.3631e-05 | 0 | #DIV/0!
|  | All Fire Risk Infractions | 0.062851 | 0.0048607 | 0.037772 | 0.032995 | 0.00015294 | 0.3038 | 1 | 0.0015655 | 0.08944 | 0.00012545 | 0.00084282 | #DIV/0!
5-year average findings and counts | System | Emergency (0-3 days) | 92.2 | 121.6 | 34.8 | 16.8 | 0 | 90 | 0 | 0 | 1 | 0 | 0 | #DIV/0!
|  | Priority (4-30 days) | 34 | 112.6 | 30.2 | 67.6 | 2 | 1476 | 0 | 11 | 65.8 | 0.6 | 1.6 | #DIV/0!
|  | Non-critical | 2766.6 | 861.2 | 806.2 | 339.2 | 0 | 6572 | 1.5 | 13 | 432.4 | 1.2 | 0 | #DIV/0!
|  | Fire Risk Infractions | 2892.8 | 1095.4 | 871.2 | 423.6 | 2 | 8138 | 1.5 | 24 | 499.2 | 1.8 | 1.6 | #DIV/0!
|  | Inspection Count | 46026 | 225359.8 | 23065 | 12838.4 | 13077 | 26787 | 1.5 | 15330.8 | 5581.4 | 14348.8 | 1898.4 | #DIV/0!
Forecast Avoidance per RAMP Forecast
2024 | HFTD | Total Inspections | 16390 | 86122 | 2000 | 11596 | 18000 | 13500 | 0 | 7024 | 2715 | 6565 | 1792
| Tier 3 | Emergency (0-3 days) | 20.6732 | 21.2439 | 1.9931 | 15.1742 | 0 | 9.75 | 0 | 0 | 0.13957 | 0 | 0
|  | Priority (4-30 days) | 7.6235 | 19.6715 | 1.7296 | 61.0582 | 0 | 146.25 | 0 | 1.7055 | 9.1838 | 0.088649 | 1.5103
|  | Non-critical | 620.3301 | 150.4541 | 46.1734 | 306.3749 | 0 | 819 | 0 | 2.0156 | 60.3504 | 0.1773 | 0
|  | All Fire Risk Infractions | 648.6268 | 191.3695 | 49.8962 | 382.6073 | 0 | 975 | 0 | 3.7211 | 69.6737 | 0.26595 | 1.5103
|  | Est. Inspection Count | 10320 | 39371 | 1321 | 11596 | 0 | 22000 | 0 | 2377 | 779 | 2120 | 1792
|  | Est. faults avoided | 10.8548 | 9.9816 | 1.0407 | 9.7239 | 0 | 6.3648 | 0 | 0.076438 | 0.63683 | 0.26595 | 0.061621
|  | Est. Ign avoided | 0.31588 | 0.29047 | 0.030286 | 0.28297 | 0 | 0.18522 | 0 | 0.0070629 | 0.058843 | 0.024573 | 0.0056938
| Tier 2 | Emergency (0-3 days) | 12.1595 | 25.226 | 1.0245 | 0 | 0 | 9.75 | 0 | 0 | 0.34687 | 0 | 0
|  | Priority (4-30 days) | 4.484 | 23.3589 | 0.88904 | 0 | 2.7529 | 146.25 | 0 | 3.3343 | 22.8238 | 0.18587 | 0
|  | Non-critical | 364.8647 | 178.6564 | 23.7334 | 0 | 0 | 819 | 0 | 3.9405 | 149.985 | 0.37174 | 0
|  | All Fire Risk Infractions | 381.5082 | 227.2413 | 25.6469 | 0 | 2.7529 | 975 | 0 | 7.2748 | 173.1557 | 0.55761 | 0
|  | Est. Inspection Count | 6070 | 46751 | 679 | 0 | 18000 | 0 | 0 | 4647 | 1936 | 4445 | 0
|  | Est. faults avoided | 6.3846 | 11.8527 | 0.53495 | 0 | 2.7529 | 2.5459 | 0 | 0.14944 | 1.5827 | 0.55761 | 0
|  | Est. Ign avoided | 0.16281 | 0.30224 | 0.013641 | 0 | 0.0702 | 0.064921 | 0 | 0.013808 | 0.14624 | 0.051523 | 0
| Non-HFTD | Emergency (0-3 days) | 63.0572 | 74.6484 | 30.4396 | 0.060194 | 0 | 9.75 | 0 | 0 | 0.6631 | 0 | 0
|  | Priority (4-30 days) | 23.2532 | 69.1235 | 26.416 | 0.24221 | 0 | 146.25 | 0 | 5.6504 | 43.6317 | 0.30743 | 0
|  | Non-critical | 1892.1269 | 528.6778 | 705.1847 | 1.2154 | 0 | 819 | 0 | 6.6777 | 286.7224 | 0.61485 | 0
|  | All Fire Risk Infractions | 1978.4374 | 672.4496 | 762.0403 | 1.5178 | 0 | 975 | 0 | 12.3281 | 331.0172 | 0.92228 | 0
|  | Est. Inspection Count | 31478 | 138345 | 20175 | 46 | 0 | 0 | 0 | 7875 | 3701 | 7352 | 0
|  | Est. faults avoided | 33.1093 | 35.0743 | 15.8948 | 0.038574 | 0 | 2.5459 | 0 | 0.25324 | 3.0256 | 0.92228 | 0
|  | Est. Ign avoided | 0.37745 | 0.39985 | 0.1812 | 0.00043974 | 0 | 0.029023 | 0 | 0.0070401 | 0.084111 | 0.025639 | 0
2023 | HFTD | Total Inspections | 11816 | 86122 | 63 | 11864 | 18000 | 28500 | 0 | 7024 | 2715 | 6565 | 1792
| Tier 3 | Emergency (0-3 days) | 14.9039 | 21.2439 | 0.063369 | 15.5249 | 0 | 9.75 | 0 | 0 | 0.13957 | 0 | 0
|  | Priority (4-30 days) | 5.496 | 19.6715 | 0.054992 | 62.4693 | 0 | 146.25 | 0 | 1.7055 | 9.1838 | 0.088649 | 1.5103
|  | Non-critical | 447.2147 | 150.4541 | 1.468 | 313.4556 | 0 | 819 | 5 | 2.0156 | 60.3504 | 0.1773 | 0
|  | All Fire Risk Infractions | 467.6147 | 191.3695 | 1.5864 | 391.4499 | 0 | 1974.7265 | 5 | 3.7211 | 69.6737 | 0.26595 | 1.5103
|  | Est. Inspection Count | 7440 | 39371 | 42 | 11864 | 0 | 6500 | 5 | 2377 | 779 | 2120 | 1792
|  | Est. faults avoided | 7.8256 | 9.9816 | 0.033089 | 9.9487 | 0 | 6.3648 | 0.017 | 0.076438 | 0.63683 | 0.26595 | 0.061621
|  | Est. Ign avoided | 0.22772 | 0.29047 | 0.0009629 | 0.28951 | 0 | 0.18522 | 0.0004947 | 0.0070629 | 0.058843 | 0.024573 | 0.0056938
| Tier 2 | Emergency (0-3 days) | 8.7661 | 25.226 | 0.031684 | 0 | 0 | 9.75 | 0 | 0 | 0.34687 | 0 | 0
|  | Priority (4-30 days) | 3.2326 | 23.3589 | 0.027496 | 0 | 2.7529 | 146.25 | 0 | 3.3343 | 22.8238 | 0.18587 | 0
|  | Non-critical | 263.0392 | 178.6564 | 0.73402 | 0 | 0 | 819 | 0 | 3.9405 | 149.985 | 0.37174 | 0
|  | All Fire Risk Infractions | 275.0379 | 227.2413 | 0.7932 | 0 | 2.7529 | 975 | 0 | 7.2748 | 173.1557 | 0.55761 | 0
|  | Est. Inspection Count | 4376 | 46751 | 21 | 0 | 18000 | 22000 | 0 | 4647 | 1936 | 4445 | 0
|  | Est. faults avoided | 4.6028 | 11.8527 | 0.016545 | 0 | 2.7529 | 2.5459 | 0 | 0.14944 | 1.5827 | 0.55761 | 0
|  | Est. Ign avoided | 0.11737 | 0.30224 | 0.00042189 | 0 | 0.0702 | 0.064921 | 0 | 0.013808 | 0.14624 | 0.051523 | 0
| Non-HFTD | Emergency (0-3 days) | 62.6185 | 74.6484 | 30.4834 | 0.05496 | 0 | 0 | 0 | 0 | 0.6631 | 0 | 0
|  | Priority (4-30 days) | 23.0914 | 69.1235 | 26.454 | 0.22115 | 0 | 0 | 0 | 5.6504 | 43.6317 | 0.30743 | 0
|  | Non-critical | 1878.963 | 528.6778 | 706.1983 | 1.1097 | 0 | 0 | 0 | 6.6777 | 286.7224 | 0.61485 | 0
|  | All Fire Risk Infractions | 1964.6729 | 672.4496 | 763.1357 | 1.3858 | 0 | 0 | 0 | 12.3281 | 331.0172 | 0.92228 | 0
|  | Est. Inspection Count | 31259 | 138345 | 20204 | 42 | 0 | 0 | 0 | 7875 | 3701 | 7352 | 0
|  | Est. faults avoided | 32.879 | 35.0743 | 15.9176 | 0.035219 | 0 | 0 | 0 | 0.25324 | 3.0256 | 0.92228 | 0
|  | Est. Ign avoided | 0.37482 | 0.39985 | 0.18146 | 0.0004015 | 0 | 0 | 0 | 0.0070401 | 0.084111 | 0.025639 | 0
2022 | HFTD | Total Inspections | 18055 | 86000 | 380 | 12380 | 18000 | 22000 | 0 | 6312 | 2087 | 6154 | 1654 | 500
| Tier 3 | Emergency (0-3 days) | 22.7726 | 21.2137 | 0.3787 | 16.2001 | 0 | 0 | 0 | 0 | 0.11538 | 0 | 0 | 0
|  | Priority (4-30 days) | 8.3977 | 19.6436 | 0.32865 | 65.1863 | 0 | 0 | 0 | 1.43 | 7.5922 | 0.083338 | 1.394 | 0
|  | Non-critical | 683.3248 | 150.2401 | 8.7733 | 327.0887 | 0 | 0 | 0 | 1.69 | 49.8917 | 0.16668 | 0 | 1
|  | All Fire Risk Infractions | 714.4951 | 191.0973 | 9.4807 | 408.4752 | 0 | 0 | 0 | 3.12 | 57.5993 | 0.25001 | 1.394 | 1
|  | Est. Inspection Count | 11368 | 39315 | 251 | 12380 | 0 | 0 | 0 | 1993 | 644 | 1993 | 1654 | 50
|  | Est. faults avoided | 11.9571 | 9.9674 | 0.19775 | 10.3814 | 0 | 0 | 0 | 0.06409 | 0.52647 | 0.25001 | 0.056876 | 0.0034
|  | Est. Ign avoided | 0.34795 | 0.29005 | 0.0057545 | 0.3021 | 0 | 0 | 0 | 0.0059219 | 0.048646 | 0.023101 | 0.0052553 | 0.00031416
| Tier 2 | Est. Emergency (0-3 days) | 13.3955 | 25.1904 | 0.19463 | 0 | 0 | 70.6186 | 0 | 0 | 0.25854 | 0 | 0 | 0
|  | Est. Priority (4-30 days) | 4.9398 | 23.3259 | 0.16891 | 0 | 2.7529 | 1066.5847 | 0 | 3.0989 | 17.0118 | 0.17399 | 0 | 0
|  | Est. Non-critical | 401.9522 | 178.4041 | 4.509 | 0 | 0 | 5462.7967 | 0 | 3.6624 | 111.7915 | 0.34799 | 0 | 9
|  | Est. All Fire Risk Infractions | 420.2875 | 226.9205 | 4.8725 | 0 | 2.7529 | 6600 | 0 | 6.7613 | 129.0618 | 0.52198 | 0 | 9
|  | Est. Inspection Count | 6687 | 46685 | 129 | 0 | 18000 | 22000 | 0 | 4319 | 1443 | 4161 | 0 | 450
|  | Est. faults avoided | 7.0335 | 11.8359 | 0.10163 | 0 | 2.7529 | 22.44 | 0 | 0.13889 | 1.1797 | 0.52198 | 0 | 0.0306
|  | Est. Ign avoided | 0.17936 | 0.30182 | 0.0025916 | 0 | 0.0702 | 0.57222 | 0 | 0.012833 | 0.109 | 0.048231 | 0 | 0.0028274
| Non-HFTD | Emergency (0-3 days) | 44.6557 | 73.764 | 30.5045 | 0.0039257 | 0 | 0 | 0 | 0 | 0.57297 | 0 | 0 | 0
|  | Priority (4-30 days) | 16.4674 | 68.3045 | 26.4723 | 0.015796 | 0 | 0 | 0 | 5.6698 | 37.7017 | 0.30856 | 0 | 0
|  | Non-critical | 1339.961 | 522.4144 | 706.6877 | 0.079262 | 0 | 0 | 0 | 6.7006 | 247.7542 | 0.61711 | 0 | 0
|  | All Fire Risk Infractions | 1401.0841 | 664.483 | 763.6645 | 0.098984 | 0 | 0 | 0 | 12.3704 | 286.0289 | 0.92567 | 0 | 0
|  | Est. Inspection Count | 22292 | 136706 | 20218 | 3 | 0 | 0 | 0 | 7902 | 3198 | 7379 | 0 | 0
|  | Est. faults avoided | 23.4473 | 34.6588 | 15.9286 | 0.0025157 | 0 | 0 | 0 | 0.25411 | 2.6144 | 0.92567 | 0 | 0
|  | Est. Ign avoided | 0.2673 | 0.39511 | 0.18159 | 2.8679e-05 | 0 | 0 | 0 | 0.0070642 | 0.072679 | 0.025734 | 0 | 0
2021 Actuals | HFTD | Total Inspections | 22354 | 86490 | 8721 | 11535 | 17068 | 20823 | 0 | 6423 | 1957 | 6239 | 1652 | 805
| Tier 3 | Emergency (0-3 days) | 0 | 1 | 1 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 11 | 3 | 2 | 27 | 0 | 45 | 0 | 1 | 17 | 0 | 0 | 7
|  | Non-critical | 425 | 175 | 23 | 434 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 3
|  | All Fire Risk Infractions | 157 | 73 | 6 | 234 | 0 | 155 | 0 | 1 | 17 | 0 | 0 | 10
|  | Est. Inspection Count | 9726 | 39550 | 3830 | 11533 | 0 | 520 | 0 | 2016 | 428 | 2014 | 1652 | 37
|  | Est. faults avoided | 1.8938 | 1.1254 | 0.5678 | 2.5772 | 0 | 1.2512 | 0 | 0.0408 | 0.6936 | 0 | 0 | 0.2958
|  | Est. Ign avoided | 0.05511 | 0.032749 | 0.016523 | 0.074997 | 0 | 0.03641 | 0 | 0.0037699 | 0.064089 | 0 | 0 | 0.027332
| Tier 2 | Emergency (0-3 days) | 7 | 0 | 1 | 0 | 0 | 87 | 0 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 12 | 2 | 3 | 0 | 0 | 1314 | 0 | 0 | 27 | 0 | 0 | 3
|  | Non-critical | 891 | 278 | 67 | 0 | 23 | 6730 | 0 | 0 | 222 | 0 | 0 | 49
|  | All Fire Risk Infractions | 305 | 162 | 14 | 0 | 22 | 8131 | 0 | 0 | 249 | 0 | 0 | 52
|  | Est. Inspection Count | 12628 | 46940 | 4891 | 2 | 17068 | 20303 | 10 | 4407 | 1529 | 4225 | 0 | 768
|  | Est. faults avoided | 6.375 | 1.0268 | 0.7582 | 0 | 22 | 27.6454 | 0 | 0 | 1.8564 | 0 | 0 | 0.289
|  | Est. Ign avoided | 0.16256 | 0.026183 | 0.019334 | 0 | 0.561 | 0.70496 | 0 | 0 | 0.17153 | 0 | 0 | 0.026704
| Non-HFTD | Emergency (0-3 days) | 18 | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 30 | 21 | 18 | 0 | 0 | 0 | 0 | 2 | 42 | 0 | 0 | 0
|  | Non-critical | 2418 | 850 | 133 | 0 | 0 | 0 | 0 | 0 | 511 | 0 | 0 | 0
|  | All Fire Risk Infractions | 1149 | 561 | 49 | 0 | 0 | 0 | 0 | 2 | 553 | 0 | 0 | 0
|  | Est. Inspection Count | 23060 | 136706 | 12292 | 0 | 0 | 0 | 0 | 7902 | 3994 | 7379 | 0 | 0
|  | Est. faults avoided | 16.7892 | 7.8268 | 1.5946 | 0 | 0 | 0 | 0 | 0.0816 | 3.451 | 0 | 0 | 0.289
|  | Est. Ign avoided | 0.1914 | 0.089226 | 0.018178 | 0 | 0 | 0 | 0 | 0.0022685 | 0.095938 | 0 | 0 | 0.0080342
2020 Actuals | HFTD | Total Inspections | 17932 | 86122 | 15698 | 11012 | 13077 | 26787 | 2 | 6940 | 2679 | 6481 | 1957 | 1415
| Tier 3 | Emergency (0-3 days) | 4 | 1 | 5 | 1 | 0 | 90 | 0 | 0 | 0 | 0 | 0 | 1
|  | Priority (4-30 days) | 18 | 0 | 10 | 59 | 2 | 1476 | 0 | 0 | 33 | 0 | 1 | 0
|  | Non-critical | 155 | 0 | 16 | 192 | 0 | 6572 | 0 | 0 | 6 | 0 | 0 | 24
|  | All Fire Risk Infractions | 177 | 1 | 31 | 252 | 2 | 8138 | 0 | 0 | 39 | 0 | 1 | 25
|  | Inspection Count | 9055 | 39371 | 10368 | 10993 | 13077 | 26787 | 0 | 2380 | 1191 | 2123 | 1957 | 1415
|  | Faults avoided | 2.8934 | 0.408 | 2.5024 | 3.468 | 2 | 27.6692 | 0 | 0 | 1.3668 | 0 | 0.0408 | 0.4896
|  | Ignitions avoided | 0.084198 | 0.011873 | 0.07282 | 0.10092 | 0.0582 | 0.80517 | 0 | 0 | 0.12629 | 0 | 0.0037699 | 0.045239
| Tier 2 | Emergency (0-3 days) | 14 | 10 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 15 | 7 | 5 | 0 | 0 | 0 | 0 | 0 | 41 | 0 | 0
|  | Non-critical | 333 | 4 | 7 | 1 | 0 | 0 | 2 | 0 | 242 | 0 | 0
|  | All Fire Risk Infractions | 362 | 21 | 14 | 1 | 0 | 0 | 2 | 0 | 283 | 0 | 0
|  | Inspection Count | 8877 | 46751 | 5330 | 19 | 0 | 0 | 2 | 4560 | 1488 | 4358 | 0
|  | Faults avoided | 7.4562 | 4.3792 | 1.0438 | 0.0034 | 0 | 0 | 0.0068 | 0 | 2.4956 | 0 | 0
|  | Ignitions avoided | 0.19013 | 0.11167 | 0.026617 | 8.67e-05 | 0 | 0 | 0.0001734 | 0 | 0.23059 | 0 | 0
| Non-HFTD | Emergency (0-3 days) | 12 | 38 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 35 | 81 | 30 | 3 | 0 | 0 | 0 | 0 | 30 | 0 | 0
|  | Non-critical | 921 | 755 | 19 | 0 | 0 | 0 | 0 | 0 | 301 | 0 | 0
|  | All Fire Risk Infractions | 968 | 874 | 64 | 3 | 0 | 0 | 0 | 0 | 331 | 0 | 0
|  | Inspection Count | 29147 | 138345 | 7802 | 105 | 0 | 0 | 0 | 7997 | 2679 | 7515 | 0
|  | Faults avoided | 9.4554 | 21.3758 | 7.4086 | 0.1224 | 0 | 0 | 0 | 0 | 2.2474 | 0 | 0
|  | Ignitions avoided | 0.10779 | 0.24368 | 0.084458 | 0.0013954 | 0 | 0 | 0 | 0 | 0.062478 | 0 | 0
Historical Data for Calculations
2019 | System | Emergency (0-3 days) | 24 | 146 | 14 | 2 |  | 23 | 0 | 0 | 0 | 0 | 0
|  | Priority (4-30 days) | 31 | 62 | 6 | 41 |  | 321 | 0 | 6 | 143 | 0 | 0
|  | Non-critical | 2483 | 798 | 356 | 368 |  | 789 | 1 | 1 | 424 | 2 | 0
|  | All Fire Risk Infractions | 2538 | 1006 | 376 | 411 |  | 1133 | 1 | 7 | 567 | 2 | 0
|  | Inspection Count | 48445 | 224018 | 22051 | 12502 |  | 10524 | 1 | 15188 | 5068 | 14206 | 1906
2018 | System | Emergency (0-3 days) | 45 | 126 | 25 | 60 |  |  |  | 0 | 1 | 0 | 0
|  | Priority (4-30 days) | 40 | 119 | 37 | 102 |  |  |  | 8 | 88 | 0 | 0
|  | Non-critical | 2254 | 893 | 716 | 211 |  |  |  | 0 | 448 | 0 | 0
|  | All Fire Risk Infractions | 2339 | 1138 | 778 | 373 |  |  |  | 8 | 537 | 0 | 0
|  | Inspection Count | 43595 | 224789 | 23941 | 14234 |  |  |  | 15313 | 6195 | 14331 | 1908
2017 | System | Emergency (0-3 days) | 50 | 112 | 45 | 19 |  |  |  | 0 | 1 | 0 | 0
|  | Priority (4-30 days) | 21 | 138 | 34 | 64 |  |  |  | 0 | 16 | 3 | 3
|  | Non-critical | 2561 | 902 | 997 | 385 |  |  |  | 5 | 325 | 0 | 0
|  | All Fire Risk Infractions | 2632 | 1152 | 1076 | 468 |  |  |  | 5 | 342 | 3 | 3
|  | Inspection Count | 42204 | 225308 | 22273 | 15952 |  |  |  | 15327 | 5069 | 14345 | 1886
2016 | System | Emergency (0-3 days) | 100 | 147 | 37 | 2 |  |  |  | 0 | 1 | 0 | 0
|  | Priority (4-30 days) | 52 | 154 | 33 | 72 |  |  |  | 3 | 13 | 0 | 3
|  | Non-critical | 3261 | 1065 | 1375 | 540 |  |  |  | 31 | 312 | 0 | 0
|  | All Fire Risk Infractions | 3413 | 1366 | 1445 | 614 |  |  |  | 34 | 326 | 0 | 3
|  | Inspection Count | 47684 | 225950 | 22191 | 10511 |  |  |  | 15346 | 4984 | 14364 | 1896
2015 | System | Emergency (0-3 days) | 242 | 77 | 53 |  |  |  |  | 0 | 2 | 0 | 0
|  | Priority (4-30 days) | 26 | 90 | 41 |  |  |  |  | 38 | 69 | 0 | 2
|  | Non-critical | 3274 | 648 | 587 |  |  |  |  | 28 | 653 | 4 | 0
|  | All Fire Risk Infractions | 3542 | 815 | 681 |  |  |  |  | 66 | 724 | 4 | 2
|  | Inspection Count | 48202 | 226734 | 24869 |  |  |  |  | 15480 | 6591 | 14498 | 1896
Note on D2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Updated distribution ignition rates 12/15/2020. Updated transmission ignition rates on 1/6/21.
Note on B3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: if time to repair has changed to 10 days, recalculated the fail assumption for emergency (=3x priority fail assumption)
Note on A5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: from CMP study
Note on G8: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: No historical ignitions
Note on A16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: established programs, cycle is not included in calculations (marked blue)
Note on H16: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: cycle is not applicable to calculations based on the assumption that findings found through IR can only be found through IR and are invisible to the naked eye.
Note on A25: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Per avg ignition counts at the top
Note on A26: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: findings by priority per inspection count
Note on A58: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Galloway, Kevin R The DIAR program is currently scheduled to stop flights at the end of 2022 and drone flights will start in 2023 asw part of the CMP program. How would you like to handle this with TCM taking over flights in 2023?
Note on I125: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: data as of 6/15, need update? Reply: Updated for 2020 only

## Master_Table
Pre-Mitigated LoRE and CoRE
| LoRE | CoRE | CoRE - Safety | CoRE - Reliability | CoRE - Financial | CoRE - Stakeholder | Total Risk Score
PSPS Overall | 4 | 1429.5137 | 13.3289 | 788.8569 | 627.3279 | 0 | 5718.0548
PSPS Tier 2 | 4 | 438.4839 | 3.9987 | 246.2869 | 188.1984 | 0 | 1753.9357
PSPS Tier 3 | 4 | 991.0298 | 9.3303 | 542.57 | 439.1295 | 0 | 3964.1191
Wildfire Non-HFTD | 7.2 | 34.4645 | 12.221 | 2.875 | 19.3685 | 0 | 248.1443
WildFire Overall | 19.2 | 805.901 | 293.75 | 46.599 | 465.5521 | 0 | 15473.3
WildFire Tier 2 | 5.8 | 955.122 | 348.0287 | 55.5172 | 551.5761 | 0 | 5539.7075
WildFire Tier 3 | 6.2 | 1562.1691 | 569.9101 | 89.0323 | 903.2267 | 0 | 9685.4482

## GeneratorGrantProgram
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.11.1 | SDGE-Risk-1-C14/M8-T1/M8-T2 | Resiliency Grant Programs/Generator Grant Program | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | Yes | 4 | 438.4839 | 3.9987 | 246.2869 | 188.1984 | 0 | 1753.9357
|  |  | PSPS Tier 3 | Yes | 4 | 991.0298 | 9.3303 | 542.57 | 439.1295 | 0 | 3964.1191
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Wildfire Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Source
Tier 3
Tier 2
Non HFTD
Total, System-Wide
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years)
Tier 3
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | 2022 Residential/Industrial/Commercial | 2022 Essential | 2022 Urgent | 2022 Medical Baseline | 2023 Residential/Industrial/Commercial | 2023 Essential | 2023 Urgent | 2023 Medical Baseline | Projected 2024 Residential/Industrial/Commercial | Projected 2024 Essential | Projected 2024 Urgent | Projected 2024 Medical Baseline | Pre PSPS LoRE | Pre PSPS CoRE Safety | Pre PSPS CoRE Reliability | Pre PSPS CoRE Financial | Pre PSPS CoRE | Extent of PSPS mitigation (Effectiveness) | PSPS Risk Reduced | Lifetime benefit | 2022 O&M Cost ($M) | 2022 Capital Cost ($M) | 2023 O&M Cost ($M) | 2023 Capital Cost ($M) | 2024 O&M Cost ($M) | 2024 Capital Cost ($M)
Source | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | Master Inputs |  |  |  | Calculated | SME | Calculated | SME | SME | SME | SME | SME | SME | SME
Tier 3 | 0 | 150 | 0 | 900 | 0 | 72.2857 | 0 | 433.7143 | 0 | 72.8571 | 0 | 437.1429 | 1 | 8.5001 | 827.4928 | 40.1394 | 216.2766 | 40% | 86.5106 | 10 | 3.64 |  | 3.64 |  | 2.517
Tier 2 | 0 | 650 | 0 | 2971.4286 | 0 | 311.3333 | 0 | 1423.2381 | 0 | 313.3333 | 0 | 1432.381 | 0.5 | 31.4661 | 3431.9693 | 157.8766 | 890.1761 | 40% | 178.0352 | 10 | 6.76 |  | 6.76 |  | 5.033
Non HFTD | [18 empty] | 0 | 10
Total, System-Wide | [7 empty] | 2240.5714 |  |  |  | 2255.7143 | [8 empty] | 10.4 |  | 7.8924 |  | 10.4
PSPS Risk Reduction |  |  |  |  | O&M Cost ($M) | Capital Cost ($M) | Total Cost ($M) | Discounted Time | PSPS risk reduced | Risk Reduction | RSE (per million $) | RSE 2024 Only (per million)
Tier 3 |  |  |  |  | 2.517 | 0 | 2.517 | 8.5302 | 86.5106 | 86.5106 | 293.1877 | 293.1877
Tier 2 |  |  |  |  | 5.033 | 0 | 5.033 | 8.5302 | 178.0352 | 178.0352 | 301.7438 | 301.7438
Non HFTD |  |  |  |  | 0 | 0 | 0 | 8.5302 | 0 | 0 | - | 0
Total, System-Wide | [13 empty] | Units
[14 empty] | Tier 3 | 1050 | 506 | 510
[14 empty] | Tier 2 | 1950 | 934 | 940
[19 empty] | Projected 2022 Residential/Industrial/Commercial | Projected 2022 Essential | Projected 2022 Urgent | Projected 2022 Medical Baseline | Sum | Resi | Essential | Urgent | Medical
[18 empty] | Tier 3 | 0 | 150 | 0 | 900 | 1050 | 0 | 0.14286 | 0 | 0.85714
[18 empty] | Tier 2 | 0 | 350 | 0 | 1600 | 1950 | 0 | 0.33333 | 0 | 1.5238
O&M Only
[17 empty] | PTY 2024 | PTY ¦ 2025 | PTY ¦ 2026 | PTY ¦ 2027 |  |  | 2024 | 2025 | 2026 | 2027
[16 empty] | O&M Escalation Rate² | 6.785% | 1.665% | 2.107% | 2.265% |  | Tier 3 | 2.6878 | 2.7325 | 2.7901 | 2.8533
[16 empty] | Capital Additions ¦ Electric Distribution¹ | 11.33% | 1.254% | 1.64% | 2.112% |  | Tier 2 | 5.3745 | 5.464 | 5.5791 | 5.7055

## PM SME Assignments (hidden)
Mitigation Initiative | Lead SME Listed for Mitigation | Other Resources (PMs, SMEs) Include in Meeting |  |  | SMEs update -- change to Yes after you validate | Minal update -- change to Yes after you validate | Kris Bourbois to provide updates -- change to Yes after you validate | Luke Kristensen to provide updates -- change to Yes after you validate | Link to Sheet | PM NOTES
SCADA Capacitor | Paul Greco | Barbara Kritzik | Jesus Acevedo |  | Yes | Yes | N/A | Yes | SCADA_Capacitors | GS: no O&M cost needed; still need 2023 capital cost information
Lightning Arrestor | Paul Greco | Lorie Azar | Victor Valencia |  | No | Yes | N/A | Yes | LightningArrestorsRemovalReplac | no O&M needed
Wireless Fault Indicators | Paul Greco | Chris Brown |  |  | No | Yes | N/A | No | WirelessFaultIndicators
Hotline Clamps | Paul Greco | Jason Hom |  |  | No | Yes | Yes | No | HotLineClamps
Expulsion Fuse Replacement | Paul Greco | Chris Brown |  |  | No | Yes | N/A | Yes | ExpulsionFuseReplacement
Infrastructure Protection Teams | Richie Viehl |  |  |  | No | Yes | Yes | N/A | InfrastructureProtectionTeams | where did tier cost breakdown come from? not adding up
Distribution Underbuilt | John Baranowski | Myles Still | Jennifer Ebner |  | No | Yes | N/A | Yes | DistributionUnderbuilt
Pole Brushing | Jimmie Webb |  | Landy Cui |  | No | No | Yes | N/A | PoleBrushing
Advanced Protection | Chris Bolton | Kenneth Fridley | Sergio Castro-Flores |  | No | Yes | N/A | Yes | AdvancedProtection
Detailed Inspections of Vegetation | Mike Daleo | Don Akau | Landy Cui |  | Yes | N/A | Yes | N/A | Detailed inspections of vegetat
Enhanced Vegetation | Mike Daleo | Don Akau | Landy Cui |  | Yes | N/A | Yes | N/A | EnhancedVegetationManagement
Fuel Management Slash Program | Mike Daleo | Don Akau | Landy Cui |  | No | N/A | Yes | N/A | Fuel Management Slash Program | Need PM to breakdown cost by tier
Distribution Drone | Jennifer Kaminsky | Jennifer Hampson | Kris Bourbois |  | No | N/A | Yes | Yes | DSI_DroneInspections
Distribution CMP 10 yr Intrusive | Jason Hom |  |  |  | No | N/A | Yes | Yes | DSI_CMP_10yrIntrusive
Distribution Annual Patrol | Jason Hom |  |  |  | No | N/A | Yes | Yes | DSI_CMP_AnnualPatrol
Distribution Tier 3 HFTD QAQC Inspections | Jason Hom |  |  |  | No | N/A | Yes | Yes | DSI_HFTD_QAQC_Tier3
Distribution CMP 5 year | Jason Hom |  |  |  | No | N/A | Yes | Yes | DSI_CMP_5yr
Distribution Infrared Inspections | Jason Hom |  |  |  | No | N/A | Yes | N/A | DSI_Infrared_Corona
Standby Power Programs | Clark Beyer | Kimberly Siebenthal |  |  | Yes | N/A | Yes | N/A | StandbyPowerPrograms | GS: no capital cost needed
Generator Grant Program | Jon Kochik | Cindy Smith |  |  | No | N/A | Yes | N/A | GeneratorGrantProgram
Generator Assistance Program | Jon Kochik | Cindy Smith |  |  | No | N/A | Yes | N/A | GeneratorAssistanceProgram
Microgrids | Don Balfour |  |  |  | No | N/A | Yes | Yes | ResilienceProgram_Microgrids
PSPS Sectionalizing | Paul Greco | Kirsten Petersen |  |  | No | N/A | Yes | Yes | PSPS Sectionalizing
Strategic Undergrounding | Lynette Aquino | Mark Alfaro | Gloria Sanchez |  | Yes | Yes | Yes | Yes | Strategic_Undergrounding | Ready for prelim RSE
Covered Conductor | Willie Thomas | Sam Adams |  |  | Yes | Yes | Yes | Yes | CoveredConductors | Ready for prelim RSE
Traditional OH Hardening | Willie Thomas | Sam Adams |  |  | Yes | Yes | Yes | Yes | Traditional_Hardening | Ready for prelim RSE
Transmission OH Hardening | John Baranowski | Jennifer Ebner |  |  | No | Yes | N/A | Yes | TransmisOHhardening |  | What's the difference between this one and distribution underbuilt? [AC]
Transmission UG Hardening | John Baranowski | Jennifer Ebner |  |  | No | Yes | N/A | No | TransmissionUGhardening |  | What's the difference between this one and distribution underbuilt? [AC]
Transmission Detailed inspections | Kevin Galloway | Monica Curry |  |  | No | N/A | Yes | Yes | TransmissionDetailed
Transmission Patrols | Kevin Galloway | Monica Curry |  |  | No | N/A | Yes | Yes | TransmissionPatrols |  | No capital $ in table 12
Transmission Infrared | Kevin Galloway | Monica Curry |  |  | No | N/A | Yes | Yes | TransmissionInfrared
Transmission Aerial 69kVI | Kevin Galloway | Monica Curry |  |  | No | N/A | Yes | Yes | AddTransAerial69kVI
Transmission Drone | Jennifer Kaminsky | Jennifer Hampson |  |  | No | N/A | Yes | Yes | DroneAssessmentTransmission
Transmission CNF Hardening | Myles Still | Tim Knowd |  |  | No | Yes | Yes | Yes | CNFTranmissionHardening |  | No previous break-out in table 12 of 2021....
Distribution CNF UG Hardening | Myles Still | Tim Knowd |  |  | No | Yes | Yes | N/A | CNFHardening-UG
Distribution CNF OH Hardening | Myles Still | Tim Knowd |  |  | No | Yes | Yes | N/A | CNFHardening-OH | Need to confirm no capital costs in 2022 and 2023 (environmental? road work?)
Circuit Ownership | Nicole Bavard | Kevin Roll |  | SG confirmed no RSE |  |  |  | Yes | DSI_CircuitOwnership - No RSE
Aviation Firefighting Program | Jesse Thrush |  |  |  | No | N/A | Yes | Yes | AviationFirefightingProg
Recloser Protocols | Shaun Gahagan | Minal |  |  | No | Yes | Yes | N/A | ReclosureProtocols
Protection Settings | Chris Bolton |  |  |  | No | Yes | Yes | N/A | ProtectionSettings
Other Special Work Procedures | Richie Viehl |  |  |  | No | Yes | Yes | No | OtherSpecialWorkProcedures
PSPS Events and Mitigation of PSPS Impacts | Katie Mauer |  |  |  | No | N/A | Yes | Yes | PSPSEventsandMitigationImpacts |  | unable to verify initiatve number of capital $ [AC]
Avian Protection | Alexander Pulido |  |  |  | No | Yes | N/A | Yes | Avian Protection

## SUG_Template (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.16 | SDG&E-Risk-1-C16/M11-T1 | Strategic Undergrounding | PSPS Overall | Yes | 4 | 1429.5137 | 13.3289 | 788.8569 | 627.3279 | 0 | 5718.0548
|  |  | PSPS Tier 2 | Yes | 4 | 438.4839 | 3.9987 | 246.2869 | 188.1984 | 0 | 1753.9357
|  |  | PSPS Tier 3 | Yes | 4 | 991.0298 | 9.3303 | 542.57 | 439.1295 | 0 | 3964.1191
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Subject Matter Expert:
Lynette Aquino
Wildfire Risk Reduction Data | Fault Rate Before Hardedning | Fault Rate After Hardening | Total Faults HFTD | Historical 5-yr Average Faults HFTD | Extrapolated Before Hardening | Extrapolated After Hardening | Historical Underground Ignitions | Historical Ignitions | 2021 units | 2021 Capital cost | 2022 units | 2022 Capital Cost | To be replaced/Forecast |  |  | Ignitions Avoided Forecast
Tier 3 | 6 | 0.2 | 293.75 | 411 | 12.93 | 6.88 | 30 | 162 | 1489 | 2.74% | 1848 |  | 2022 | 2023 | 2024 | 2022 | 2023 | 2024
Tier 2 | 5 | 0.4 | 293.75 | 411 | 12.93 |  |  |  | 0 |  | 0 |  | 50 | 78.1 | 93.8 | #REF! | #REF! | #REF!
Non HFTD | [8 empty] | 0 |  | 0
Total, System-Wide | 11 | 0.6 |  |  |  |  | 30 |  | 1489 |  | 1848
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years) |  | Data in GREEN above should derive to the values in YELLOW below
Tier 3 | 5% | #VALUE! | 0% | 0 | 25000 | 0 | 25 |  | OR SME direct input
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Tier 3
Tier 2
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years) |  | Data in GREEN above should derive to the values in YELLOW below
Tier 3 | [8 empty] | OR SME direct input
Tier 2
Total, System-Wide
Risk Spend Efficiency

## CheckHotLineClamps (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.10 | SDG&E-Risk-1-C12/M7-T1/M7-T2 | Hotline Clamps | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 5.8 | 955.122 | 348.0287 | 55.5172 | 551.5761 | 0 | 5539.7075
|  |  | WildFire Tier 3 | Yes | 6.2 | 1562.1691 | 569.9101 | 89.0323 | 903.2267 | 0 | 9685.4482
Subject Matter Expert:
Paul Greco | Emily France | Jason Hom
Wildfire Risk Reduction Data | Wire downs associated with connection failures | Ignition Rate | HLC | 2020 HLC actuals | 2021 HLC Actuals | 2022 HLC to be installed | Ratio 2020 |  |  | Ignition reduced 2020 from data | Ignition reduced 2021 from data | Ignition reduced 2022 from data | %Change in Wildfire LoRE | Ignitions reduced 2020 | Ignitions reduced in 2021 | Ignitions reduced in 2022 | %Change in Wildfire LoRE | 2020 O&M cost | 2020 Capital Cost per Unit($) | 2021 O&M cost | 2021 Capital Cost per Unit($) | 2022 O&M cost | 2022 Capital Cost per Unit($) | Total Cost 2021 (k$) | Lifetime Benefit | Target Projections for 2023 - Use in Table 12 WMP
Source | SME | Master Input | SME | SME | SME | SME | [6 empty] | Calculated | Calculated | Calculated | Calculated | Calculated | SME | SME | SME | SME | SME | SME | Calculated | SME | SME | 2023 projections do not need to be broken down by Tier
Notes | Minal
Tier 3 | 1.1294 | 2.736% | 3094 | 598 | 225 | 825 | 0.072721 | 0.082132 | 0.0022468 | 0.0011058 | 0.00041607 | 0.0015256 | 0.3047% | 0.0011111 | 0.00037037 | 0.0014815 | 0.2963% | 0 | 0.95581 | 0 | 0.534 | 0 | 2.161 | 3.6508 | 25
Tier 2 | 1.2706 | 3.37% | 5237 | 1463 | 2025 | 825 | [6 empty] | 0.0016667 | 0.0016667 | 0.0023611 | 0.00097222 | 0.5% | 0 | 2.343 | 0 | 4.809 | 0 | 2.161 | 9.313 | 25
Non HFTD | 0 | 0 | [12 empty] | #DIV/0! | #DIV/0!
Total, System-Wide | 2.4 | 0.061056 |  | 2061 | 2250 | 1650 | [17 empty] | 12.9638
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Total Cost (m$) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE
Tier 3 | 0.3047% | 6.1811 | 0% | 1421 | 0 | 0 | 3.6508 | 25 | 23.3846 | 23.3846 | 17.4131 | 111.5366
Tier 2 | 0.5% | 5.771 | 0% |  | 0 | 0 | 9.313 | 25 | 23.1324 | 23.1324 | 17.4131 | 43.2521
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Tier 3
Tier 2
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years) | PSPS Risk reduced
Tier 3 | 0% |  |  |  | 1501 | 3002 | 25 | 0
Tier 2
Total, System-Wide

## Customer Resiliency Programs (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.11.1 | SDG&E-Risk-1-C13/M8-T1 | Customer Resiliency Programs | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | Yes | 4 | 438.4839 | 3.9987 | 246.2869 | 188.1984 | 0 | 1753.9357
|  |  | PSPS Tier 3 | Yes | 4 | 991.0298 | 9.3303 | 542.57 | 439.1295 | 0 | 3964.1191
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
Subject Matter Expert:
Cindy Smith
Wildfire Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Tier 3
Tier 2
Non HFTD
Total, System-Wide
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years)
Tier 3 | 5%
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Residential/Industrial/Commercial | Essential | Urgent | Medical Baseline | Total by region | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation | PSPS Risk Reduced | Lifetime benefit | Total Cost | Target Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | SME | SME | Calculated | SME | SME | SME | Calculated | SME | SME | SME | 2023 projections do not need to be broken down by Tier
Tier 3 | 0 | 0 | 0 | 2000 |  | 1 | 176.66 |  | 0
Tier 2 | 0 | 0 | 0 | 4000 |  | 0.5 | 353.31 |  | 0
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | Lifetime Benefit (Years)
Tier 3 | [6 empty] | 10
Tier 2 | [6 empty] | 1
Total, System-Wide

## Strategic_Undergrounding
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.16 | SDG&E-Risk-1-C16/M11-T1 | Strategic Undergrounding | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | Yes | 4 | 438.4839 | 3.9987 | 246.2869 | 188.1984 | 0 | 1753.9357
|  |  | PSPS Tier 3 | Yes | 4 | 991.0298 | 9.3303 | 542.57 | 439.1295 | 0 | 3964.1191
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 5.8 | 955.122 | 348.0287 | 55.5172 | 551.5761 | 0 | 5539.7075
|  |  | WildFire Tier 3 | Yes | 6.2 | 1562.1691 | 569.9101 | 89.0323 | 903.2267 | 0 | 9685.4482
Wildfire Risk Reduction Data | Fault Rate Before Hardedning | Fault Rate After Hardening | Total Faults HFTD calculated | Historical 5-yr Average Faults HFTD | Extrapolated Before Hardening | Extrapolated After Hardening | Historical Underground Ignitions | Historical Ignitions | UG Ignition Rate | Ignition Rate | Ignitions before | Ignitions after | Ignitions reduced | 2022 Strategic Undergrounding miles mitigated / units | 2023 Strategic Undergrounding miles mitigated / units | 2024 Strategic Undergrounding forecast miles mitigated / units | 2022 O&M Cost ($M) | 2022 Capital Cost ($M) | 2023 O&M Cost ($M) | 2023 Capital Cost ($M) | 2024 O&M cost ($M) | 2024 Capital Cost ($M) | Ignitions Avoided 2022 | Ignitions Avoided 2023 | Ignitions Avoided 2024 | Lifetime benefit (years)
Source | SME | SME | SME | SME | SME | SME | SME (Ignition database 2015-2019) | SME (Ignition database 2015-2019) | Calculated | Ignition Rate Database (Master Inputs | 'Calculated | Calculated | Calculated | SME | SME | SME | SME | SME | SME | SME | SME | SME | Calculated | Calculated | Calculated | SME
Tier 3 | 9.23 | 5.12 | 283.9 | 412.8 | 13.5 | 7.49 | 3 | 98% | 2% | 4.298% | 0.58023 | 0.011605 | 0.56862 | 36.5 | 78.8 | 79 | 1.511 | 119.294 | 2.321 | 223.147 | 1.84 | 183.999 | 0.20755 | 0.44808 | 0.44921 | 40 | 0.63
Tier 2 | 9.23 | 5.12 | 283.9 | 412.8 | 13.5 | 7.49 | 3 | 98% | 2% | 4.328% | 0.58431 | 0.011686 | 0.57262 | 21.5 | 46.3 | 46 | 0.887 | 70.061 | 1.31 | 131.055 | 1.081 | 108.1 | 0.12311 | 0.26512 | 0.26341 | 40 | 0.37
Non HFTD
Total, System-Wide | [13 empty] | 58 | 125.1 | 125 | 0 | 38.79 | 0 | 69.41 | #REF! | 188.85
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend (M$) | Capex Spend ($M) | Total Cost ($M) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE (per million $)
Tier 3 | 7.245% | 5.7508 | 0% | 1562.1691 | 1.84 | 183.999 | 185.839 | 40 | 701.7474
Tier 2 | 4.542% | 5.5366 | 0% | 955.122 | 1.081 | 108.1 | 109.181 | 40 | 251.5858
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | 2022 Residential/Industrial/Commercial | 2022 Essential | 2022 Urgent | 2022 Medical Baseline | 2023 Residential/Industrial/Commercial | 2023 Essential | 2023 Urgent | 2023 Medical Baseline | Projected 2024 Residential/Industrial/Commercial | Projected 2024 Essential | Projected 2024 Urgent | Projected 2024 Medical Baseline | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation/Effectiveness | PSPS Risk Reduced | Lifetime benefit (years) | 2022 O&M Cost ($M) | 2022 Capital Cost ($M) | 2023 O&M Cost ($M) | 2023 Capital Cost ($M) | Projected 2024 O&M Cost ($M) | Projected 2024 Capital Cost ($M) | Total Cost ($M)
Source | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | Master Inputs | Calculated | SME | Calculated | SME | SME | SME | SME | SME | SME | SME | Calculated
Tier 3 | 1293.7577 | 115.2423 | 0 | 0 | 1439.3246 | 128.2087 | 0 | 0 | 1439.3246 | 128.2087 | 0 | 0 | 3.2 | 437.0829 | 100% | 1398.6651 | 40 | 1.511 | 119.294 | 2.321 | 223.147 | 1.84 | 183.999
Tier 2 | 1110.846 | 12.9634 | 0 | 0.19064 | 1235.8326 | 14.4219 | 0 | 0.21209 | 1235.8326 | 14.4219 | 0 | 0.21209 | 2.4 | 142.5705 | 100% | 342.1691 | 40 | 0.887 | 70.061 | 1.31 | 131.055 | 1.081 | 108.1
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M cost (m$) | Capital Cost (m$) | Total Cost (m$) | Lifetime benefit | Discounted Time | PSPS riskreduced | Risk Reduction | Total RSE (per million $)
Tier 3 | 0% | 3.2 | 35.28% | 282.8664 | 1.84 | 183.999 | 185.839 | 40 | 23.1148 | 1398.6651 | 2100.4125 | 261.2506 | [5 empty] | 1511 | 119294 | 2321 | 223147 | 1840 | 183999
Tier 2 | 0% | 2.4 | 19.51% | 114.7569 | 1.081 | 108.1 | 109.181 | 40 | 23.1148 | 342.1691 | 593.7549 | 125.7042 | [5 empty] | 887 | 70061 | 1310 | 131055 | 1081 | 108100
Non HFTD
Total, System-Wide
[11 empty] | 2022 | 2023 | 2024
[10 empty] | Tier 3 | 1409 | 1567.5334 | 1567.5334
[10 empty] | Tier 2 | 1124 | 1250.4666 | 1250.4666 | Original GRC 2024 | Revised GRC 2024
[10 empty] | Total | 2533 | 2818 | 2818 | 3382 | 2818.3333
[10 empty] | Tier 2 (%) | 0.55626
[10 empty] | Tier 3 (%) | 0.44374
Ratios
[10 empty] | 2022 Residential/Industrial/Commercial | 2022 Essential | 2022 Urgent | 2022 Medical Baseline | sum | resi | essential | urgent | medical
[10 empty] | 1190 | 106 | 0 | 0 | 1296 | 0.91821 | 0.08179 | 0 | 0
[10 empty] | 5827 | 68 | 0 | 1 | 5896 | 0.9883 | 0.011533 | 0 | 0.00016961
[12 empty] | PTY 2024 | PTY ¦ 2025 | PTY ¦ 2026 | PTY ¦ 2027 |  | 2024 | 2025 | 2026 | 2027
[11 empty] | O&M Escalation Rate² | 6.785% | 1.665% | 2.107% | 2.265% | Tier 3 | 1.9648 | 1.9976 | 2.0396 | 2.0858
[11 empty] | Capital Additions ¦ Electric Distribution¹ | 11.33% | 1.254% | 1.64% | 2.112% | Tier 2 | 1.1543 | 1.1736 | 1.1983 | 1.2254
[16 empty] | Tier 3 | 204.8461 | 207.414 | 210.8148 | 215.2682
[16 empty] | Tier 2 | 120.3477 | 121.8564 | 123.8544 | 126.4708

## CoveredConductors
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.4.1 | SDG&E-Risk-1-C7/M2-T1 | Covered Conductor | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | Wildfire Non-HFTD | Yes | 7.2 | 34.4645 | 12.221 | 2.875 | 19.3685 | 0 | 248.1443
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 5.8 | 955.122 | 348.0287 | 55.5172 | 551.5761 | 0 | 5539.7075
|  |  | WildFire Tier 3 | Yes | 6.2 | 1562.1691 | 569.9101 | 89.0323 | 903.2267 | 0 | 9685.4482
Wildfire Risk Reduction Data | Fault Rate Before hardening | Total Faults HFTD | Average Faults HFTD | Extrapolated Before Hardening | Faults after hardening Covered Conductor | Ignition Rate | Ignitions Before | Ignitions after | Ignitions Reduced | 2022 miles mitigated | Ignitions reduced 2022 | 2023 miles mitigated | Ignitions reduced 2023 | 2024 miles mitigated | Ignition Reduced 2024 | 2022 O&M cost ($M) | 2022 Capital Cost ($M) | 2023 O&M cost ($M) | 2023 Capital Cost ($M) | Projected 2024 O &M Cost ($M) | Projected 2024 Capital Cost ($M) | Lifetime benefit (years)
Source | SME | SME | SME | Calculated | SME | Ignition Team | IgnitionTeam | Calculated | Calculated | SME | Calculated | SME | Calculated | SME | Calculated | SME | SME | SME | SME | SME | SME | SME
Tier 3 | 6.48 | 283.9 | 412.8 | 6.48 | 2.3004 | 4.298% | 0.27851 | 0.098871 | 0.17964 | 49 | 0.088023 | 82 | 0.1473 | 49 | 0.088023 | 0.971 | 102.207 | 1.237 | 123.715 | 0.485 | 48.558 | 40 | 0.82
Tier 2 | 7.02 | 283.9 | 412.8 | 7.02 | 2.4921 | 4.328% | 0.30384 | 0.10786 | 0.19598 | 11 | 0.021558 | 18 | 0.035276 | 11 | 0.021558 | 0.218 | 22.435 | 0.272 | 27.157 | 0.107 | 10.659 | 40 | 0.18
Non HFTD
Total, System-Wide | 13.5 | [8 empty] | 60 |  | 100 |  | 60
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE (per million $)
Tier 3 | 1.42% | 6.112 | 0% | 1562.1691 | 0.485 | 48.558 | 49.043 | 40 | 137.507 | 137.507 | 23.1148 | 64.8093
Tier 2 | 0.3717% | 5.7784 | 0% | 955.122 | 0.107 | 10.659 | 10.766 | 40 | 20.5901 | 20.5901 | 23.1148 | 44.2072
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | 2020 Residential/Industrial/Commercial | 2020 Essential | 2020 Urgent | 2020 Medical Baseline | 2021 Residential/Industrial/Commercial | 2021 Essential | 2021 Urgent | 2021 Medical Baseline | Projected 2022 Residential/Industrial/Commercial | Projected 2022 Essential | Projected 2022 Urgent | Projected 2022 Medical Baseline | Total by region | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation/Effectiveness | Lifetime benefit (years) | 2020 O&M cost ($M) | 2020 Capital Cost ($M) | 2021 O&M cost ($M) | 2021 Capital Cost ($M) | Projected 2022 O &M Cost ($M) | Projected 2022 Capital Cost ($M) | Total cost ($M) | PSPS Risk Reduced | Target Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | Calculated | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | Calculated | Calculated | SME
Notes from SME
Tier 3 | [13 empty] | 1
Tier 2 | [13 empty] | 0.5
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend ($M) | Capex Spend ($M) | Total Cost ($M) | Lifetime Benefit (Years) | PSPS Risk Reduction | Risk Reduction | Discounted Time | RSE (per million $)
Tier 3
Tier 2
Non HFTD | [14 empty] | PTY 2024 | PTY ¦ 2025 | PTY ¦ 2026 | PTY ¦ 2027 |  | 2024 | 2025 | 2026 | 2027
Total, System-Wide | [13 empty] | O&M Escalation Rate² | 0.06785 | 0.016652 | 0.021068 | 0.022649 | Tier 3 | 0.51791 | 0.52653 | 0.53762 | 0.5498
[14 empty] | Capital Additions ¦ Electric Distribution¹ | 0.1133 | 0.012536 | 0.016396 | 0.021125 | Tier 2 | 0.11426 | 0.11616 | 0.11861 | 0.1213
[19 empty] | Tier 3 | 54.0596 | 54.7373 | 55.6348 | 56.8101
[19 empty] | Tier 2 | 11.8667 | 12.0154 | 12.2124 | 12.4704

## ExpulsionFuseReplacement (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.7 | SDG&E-Risk-1-C8/M3-T2 | Expulsion Fuse Replacement | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 5.8 | 955.122 | 348.0287 | 55.5172 | 551.5761 | 0 | 5539.7075 |  |  |  | when talking to hugo about data, check timeframe for GIS business services data update see if includes work all the way through present day (could have some discrepency with true total number)
|  |  | WildFire Tier 3 | Yes | 6.2 | 1562.1691 | 569.9101 | 89.0323 | 903.2267 | 0 | 9685.4482
Subject Matter Expert:
Paul Greco | Emily France
Wildfire Risk Reduction Data | Expulsion Fuses | Average Ignitions rate | Pre mitigation Ignition Rate | Number of Total Fuses Installed | Hardened prior to 2020 | Remaining Harden 2020 | 2022 actuals Fuses Installed | 2023 actuals Fuses Installed | 2024 actuals Fuses to be Installed | Ignition Reduction 2020 | Ignition Reduction 2021 | Ignition Reduction 2022 | O&M Cost 2020 ($M) | Capital Cost 2020 ($M) | O&M Cost 2021 ($M) | Capital Cost 2021 ($M) | O&M Cost 2022 ($M) | Capital Cost 2022 ($M) | Lifetime Benefit (years) | Target UNIT Projections for 2023 - Use in Table 12 WMP | 2023 projections do not need to be broken down by Tier
Source | SME | SME | Calculated | SME | SME | Calculated | SME | SME | SME | Calculated | Calculated | Calculated | SME | SME | SME | SME | SME | SME | SME | SME
Notes from SME | Minal | Minal - check the anology move from 0.4 to 0 |  | consult Chris Brown, GS to ask Hugo to put in GIS business services request | no updates |  | no updates | validate with Summer Zhou | consult Summer and Chris Brown for estimates |  |  |  | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | consult Chris Brown | consult Chris Brown for estimates
Tier 3 | 80 | 4.298% | 0.05372% | 4342 | 2769 | 1573 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0
Tier 2 | 104.2 | 4.328% | 0.04154% | 6799 | 316 | 6483 | 100 | 0 | 0 | 0.00066763 | 0 | 0 | 0 | 0.842 | 0 | 0 | 0 | 0 | 25 | 0
Non HFTD
Total, System-Wide |  |  |  | 11141 | 3085 |  | 100 | 3509 | 0 |  |  |  | 0 | 6.521 | 0 | 6.489 | 0 | 0.734 |  | 0 | no work planned for 2023
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend ($M) | Capex Spend ($M) | Total Cost ($M) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE (per million)
Tier 3 | 0% | 6.2 | 0% | 1562.1691 | 0 | 0 | 0 | 25 | 0 | 0 | 17.4131 | -
Tier 2 | 0.01151% | 5.7993 | 0% | 955.122 | 0 | 0.842 | 0.842 | 25 | 0.63766 | 0.63766 | 17.4131 | 13.1874
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation |  |  | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Tier 3
Tier 2
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value |  |  | O&M Spend ($M) | Capex Spend ($M) | Lifetime Benefit (Years)
Tier 3
Tier 2
Total, System-Wide
Note: the total of 2019-2022 fuses intallations do not equals 11141 is because some of the fuses got descoped due to various reasons or completed by other programs (FiRM/PRiME/SUG, etc)
1. Fixed Capacitor – will be replaced under Capacitor budget
2. Solid Blades/Bridged Fuse, they will be removed when rebuilding circuit and pole.
3. Current Limiting Fuse – Cal fire exempt
4. Energy Limiting Fuse - Cal fire exempt
5. Switched Capacitor – will be replaced under Capacitor budget
6. No fusing on the pole
7. Pole is no longer exist.
8. Fuse idle
9. Pole will be removed by other program in the near future
Note on B12: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: @Veldore, Vidyunmala (Contractor) can you clarify what this column is? totals? same with columne E12 just fuses number... Reply: 5yr average Operation of Expulsion Fuses for Tier
Note on I18: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 [Tasks] There is a task anchored to this comment that cannot be viewed in your client. Comment: @Zhou, Summer (Contractor) looking at the latest dashboard i see number installed in 2021 of 3509 can you please double check your source and let alex and paul know (they were on meeting we discussed this) Reply: Gillian, 3509 is installed under Fuse budget, and there are 501 fuses installed under other program. Would you like me to exclude installed by others? Reply: thanks for that update. Reply: Per confirmation with paul and alex, we want only the HFTD for this purpose because we are using cost only from HFTD budget. can you therefore go back and update the breakdown by Tier @Zhou, Summer (Contractor) . sorry for the confusion. Reply: @Semmer, Gillian M updated and excluded completed by others
Note on J18: Zhou, Summer (Contractor): It includes 66 fuses overlap with other program that is plan to be completed in 2022

## CNFHardening-OH (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.3.17.3 |  | CNF Fire Hardening - OverHead OH | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | All costs in 2020 and 2021 were in Tier 3
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 6.84 | 622.9051 | 218.7197 | 47.0778 | 345.8283 | 11.2794 | 4260.6712
|  |  | WildFire Tier 3 | Yes | 5.13 | 1409.2816 | 499.931 | 107.6064 | 790.4649 | 11.2794 | 7229.6146
Subject Matter Expert:
Myles Still | Tim Knowd
Wildfire Risk Reduction Data | Extrapolated Before Hardening (Faults per 100 miles) | Effectiveness Estimate | Extrapolated after hardening Traditional | Ignition Rate | Ignitions Before | Ignitions after | Ignitions Reduced | 2020 miles mitigated | Ignitions reduced 2020 | 2021 miles mitigated | Ignitions reduced 2021 | 2022 forecast of miles mitigation | Ignition Reduced 2022 | O&M Cost 2020 ($M) | Capital Cost 2020 ($M) | O&M Cost 2021 ($M) | Capital Cost 2021 ($M) | O&M Cost 2022 ($M) | Capital Cost 2022 ($M) | Lifetime benefit (years) | Target UNIT Projections for 2023 - Use in Table 12 WMP | Target CAPITAL Projections for 2023 - Use in Table 12 WMP | Target O&M Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | Calculated | Ignition Team | Ignition Team | Calculated | Calculated | SME | Calculated | SME | Calculated | SME | Calculated | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME
Notes from SME | Minal | Minal | Minal | Master Input | [9 empty] | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier |  |  | Luke and PM to confirm | Kris provided total, PM to confirm
Tier 3 | 13.5 | 44.5% | 7.4925 | 4.298% | 0.58023 | 0.32203 | 0.2582 | 46.75 | 0.12071 | 6.86 | 0.017713 | 0 | 0 | 0 | 45.74 | 0 | 11.31 | 0 | 0.69 | 40 | 0 | 0.21
Tier 2 | 13.5 | 44.5% | 7.4925 | 4.328% | 0.58431 | 0.32429 | 0.26002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 40 | 0 | 0
Non HFTD | [16 empty] | 0 |  | 0 |  |  | 0
Total, System-Wide | [13 empty] | 0 | 45.74 | 0 | 11.31 | 0 | 0.69 |  |  | 0.21 | 0
KB: CNFHardening O&M costs are embedded within Traditional Hardening totals
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE per million
Tier 3 | 2.698% | 4.9916 | 0% | 1409.2816 | 0 | 57.74 | 57.74 | 40 | 195.0757 | 195.0757 | 23.1148 | 78.0937
Tier 2 | 0% | 6.84 | 0% | 622.9051 | 0 | 0 | 0 | 40 | 0 | 0 | 23.1148 | -
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation | Data Category/ Calculation
Tier 3
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | PSPS Risk Reduction | Risk Reduction | Discounted Time | RSE per million
Tier 3
Tier 2
Non HFTD
Total, System-Wide
Risk Spend Efficiency

## PSPSEventsandMitigationImpacts (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.6.6 | SDG&E-Risk-1-C37-T1/C37-T2 | PSPS events and mitigation of PSPS impacts | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | 40% used for WMP previous to breaking out by tier
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | possible differention due to keeping weighted average of 40% for service territory
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A |  | GS/Katie update 1/20: ~47% Tier 3, ~53% Tier 2 breakdown following same as RAMP
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 6.84 | 622.9051 | 218.7197 | 47.0778 | 345.8283 | 11.2794 | 4260.6712
|  |  | WildFire Tier 3 | Yes | 5.13 | 1409.2816 | 499.931 | 107.6064 | 790.4649 | 11.2794 | 7229.6146
Subject Matter Expert:
Katie Mauer
Wildfire Risk Reduction Data | Mitigation Effectiveness | Lifetime Benefit (Years) | O&M Cost 2020 ($M) | Capital Cost 2020 ($M) | O&M Cost 2021 ($M) | Capital Cost 2021 ($M) | O&M Cost 2022 ($M) | Capital Cost 2022 ($M) | Target UNIT Projections for 2023 - Use in Table 12 WMP | Target CAPITAL Projections for 2023 - Use in Table 12 WMP | Target O&M Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME
Notes From SME | John Baranowski | John Baranowski | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier | Kris Bourbois provided total, PM/SME to breakdown by Tier | Luke Kristensen to provide total cost, PM/SME to breakdown by Tier |  | Kris and PM to confirm | Kris provided total, PM to confirm | Kris & Luke - these costs will include: Communication Practices Emergency Management Protocols for PSPS renergization
Tier 3 | 38% | 1 | #REF! | 0 | #REF! | 0 | #REF! | 0
Tier 2 | 68% | 1 | #REF! | 0 | #REF! | 0 | #REF! | 0
Non HFTD |  |  | 0
Total, System-Wide |  |  | #REF! |  | #REF! |  | #REF! |  |  |  | #REF!
KB: Total costs for multiple mitigations (Emergency Management, Emerg Mgt PSPS, Communication Practices, PSPS Communications, and Community Outreach & Public Awareness)
Wildfire Risk Reduction | Pre-LoRE | Pre-CORE | Mitigation Effectiveness | WF Risk Reduction | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | Risk Reduction | Discount Time | RSE per million
Tier 3 | 5.13 | 1409.2816 | 38% | 2747.2535 | #REF! | 0 | #REF! | 1 | 2747.2535 | 0.97087 | -
Tier 2 | 6.84 | 622.9051 | 68% | 2897.2564 | #REF! | 0 | #REF! | 1 | 2897.2564 | 0.97087 | -
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Residential/Industrial/Commercial | Essential | Urgent | Medical Baseline | Total by region | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation/Effectiveness | Lifetime benefit | Total cost | PSPS Risk Reduced | Target Projections for 2023 - Use in Table 12 WMP
Tier 3
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | PSPS Risk Reduced | Lifetime Benefit (Years)
Tier 3 | [6 empty] | 0
Tier 2 | [6 empty] | 0
Total, System-Wide

## ReclosureProtocols (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.6.1.1 |  |  | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Reclosure Protocols | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 6.84 | 622.9051 | 218.7197 | 47.0778 | 345.8283 | 11.2794 | 4260.6712
|  |  | WildFire Tier 3 | Yes | 5.13 | 1409.2816 | 499.931 | 107.6064 | 790.4649 | 11.2794 | 7229.6146
Subject Matter Expert:
Shaun Gahagan | Minla
Wildfire Risk Reduction Data | Estimated Faults avoided | Lifetime Benefit (Years) | O&M Cost 2020 ($M) | Capital Cost 2020 ($M) | O&M Cost 2021 ($M) | Capital Cost 2021 ($M) | O&M Cost 2022 ($M) | Capital Cost 2022 ($M) | Target UNIT Projections for 2023 - Use in Table 12 WMP | Target CAPITAL Projections for 2023 - Use in Table 12 WMP | Target O&M Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME
Notes From SME | Minal |  | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP |  | Kris and PM to confirm | Kris provided total, PM to confirm
Tier 3 | 4.3 | 1 | 0.008814 |  | 0.008814 |  | 0.008814
Tier 2 | 4.6 | 1 | 0.00763 |  | 0.00763 |  | 0.00763
Non HFTD
Total, System-Wide |  |  | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | No capital costs in Table 12 of 2021 filing [AC]
Wildfire Risk Reduction | %Change in LoRE | WF Risk Reduction | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | Risk Reduction | Discount Time | RSE per million
Tier 3 | 79.63% | 5756.9153 | 0.008814 | 0 | 0.008814 | 1 | 5756.9153 | 0.97087 | 634131.8533
Tier 2 | 63.89% | 2722.0955 | 0.00763 | 0 | 0.00763 | 1 | 2722.0955 | 0.97087 | 346371.0565
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Residential/Industrial/Commercial |  |  |  |  | Essential | Urgent | Medical Baseline | Total by region | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation/Effectiveness | Lifetime benefit | Total cost | PSPS Risk Reduced | Target Projections for 2023 - Use in Table 12 WMP
Tier 3
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % |  |  |  |  | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | PSPS Risk Reduced | Lifetime Benefit (Years)
Tier 3 | [10 empty] | 0
Tier 2 | [10 empty] | 0
Total, System-Wide

## ProtectionSettings (hidden)
2021 WMP Initiative # | RAMP ID | Initative activity | Classification | Applicable? | Pre-Mitigat. LoRE | Pre-Mitigat. CoRE | Pre-Mitigat. CoRE-Safety | Pre-Mitigat. CoRE-Reliab. | Pre-Mitigat. CoRE-Fin. | Pre-Mitigat. CoRE-Stakeh. | Pre-Mitigat. Risk Score
7.3.6.1.2 |  |  | PSPS Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 2 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | PSPS Tier 3 | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  | Sensitive/Fast Protection settings | Wildfire Non-HFTD | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Overall | No | N/A | N/A | N/A | N/A | N/A | N/A | N/A
|  |  | WildFire Tier 2 | Yes | 6.84 | 622.9051 | 218.7197 | 47.0778 | 345.8283 | 11.2794 | 4260.6712
|  |  | WildFire Tier 3 | Yes | 5.13 | 1409.2816 | 499.931 | 107.6064 | 790.4649 | 11.2794 | 7229.6146
Subject Matter Expert:
Chris Bolton
Wildfire Risk Reduction Data | Faults Isolated by fuses | Faults isolated by Profile 3 enabled device | Extreme Ignition Rate | Total Faults | Ignitions reduced | Lifetime Benefit (Years) | O&M Cost 2020 ($M) | Capital Cost 2020 ($M) | O&M Cost 2021 ($M) | Capital Cost 2021 ($M) | O&M Cost 2022 ($M) | Capital Cost 2022 ($M) | Target UNIT Projections for 2023 - Use in Table 12 WMP | Target CAPITAL Projections for 2023 - Use in Table 12 WMP | Target O&M Projections for 2023 - Use in Table 12 WMP
Source | SME | SME | SME | calculated | calculated | SME | SME | SME | SME | SME | SME | SME | SME | SME | SME
Notes From SME | Minal | Minal | Master Input |  |  |  | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP | Confirmed with Shaun to use 2021 WMP |  | Kris and PM to confirm | Kris provided total, PM to confirm
Tier 3 | 48 | 50 | 10% | 98 | 1.96 | 1 | 0.008814 |  | 0.008814 |  | 0.008814
Tier 2 | 13 | 46 | 10.34% | 59 | 1.2201 | 1 | 0.00763 |  | 0.00763 |  | 0.00763
Non HFTD
Total, System-Wide | [6 empty] | 0 |  | 0 |  | 0 |  |  |  | 0 | No costs previously filed in 2021 Table 12 [AC]
Wildfire Risk Reduction | LoRE Reduction % | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend (m$) | Capex Spend (m$) | Total Cost (m$) | Lifetime Benefit (Years) | WF Risk Reduction | Risk Reduction | Discounted Time | RSE per million
Tier 3 | 38.21% | 3.17 | 0% | 1409.2816 | 0.008814 | 0 | 0.008814 | 1 | 2762.1919 | 2762.1919 | 0.97087 | 304259.1022
Tier 2 | 17.84% | 5.6199 | 0% | 622.9051 | 0.00763 | 0 | 0.00763 | 1 | 760.019 | 760.019 | 0.97087 | 96708.0672
Non HFTD
Total, System-Wide
PSPS Risk Reduction Data | Residential/Industrial/Commercial |  |  |  |  | Essential | Urgent | Medical Baseline | Total by region | Pre PSPS LoRE | Pre PSPS CoRE | Extent of PSPS mitigation/Effectiveness |  |  |  | Lifetime benefit | Total cost | PSPS Risk Reduced | Target Projections for 2023 - Use in Table 12 WMP
Tier 3
Tier 2
Non HFTD
Total, System-Wide
PSPS Risk Reduction | LoRE Reduction % |  |  |  |  | LoRE Reduction Value | CoRE Reduction % | CoRE Reduction Value | O&M Spend | Capex Spend | PSPS Risk Reduced | Lifetime Benefit (Years)
Tier 3 | [10 empty] | 0
Tier 2 | [10 empty] | 0
Total, System-Wide