## Data
LineClass | Primary Distribution Line | Count of Cause | Column Labels
Reported | 1 | Row Labels | Bare,Other | Covered | Grand Total | Row Labels | Bare,Other | Covered | Grand Total | Bare,Other % | Covered% | Total%
|  | Anchor/Guy |  | 1 | 1 | Anchor/Guy |  | 1 | 1 | 0% | 6.25% | 2.041%
Row Labels | Count of ConductorType | Animal | 4 | 4 | 8 | Animal | 4 | 4 | 8 | 12.12% | 25% | 16.33%
Covered | 10 | Balloon | 4 | 1 | 5 | Balloon | 4 | 1 | 5 | 12.12% | 6.25% | 10.2%
Other, see comment | 12 | Conductor | 7 | 1 | 8 | Conductor | 7 | 1 | 8 | 21.21% | 6.25% | 16.33%
Grand Total | 22 | Connector Device | 3 |  | 3 | Connector Device | 3 |  | 3 | 9.091% | 0% | 6.122%
|  | Contamination | 1 |  | 1 | Contamination | 1 |  | 1 | 3.03% | 0% | 2.041%
|  | Equipment - Other | 1 | 1 | 2 | Equipment - Other | 1 | 1 | 2 | 3.03% | 6.25% | 4.082%
|  | Fuse |  | 2 | 2 | Fuse |  | 2 | 2 | 0% | 12.5% | 4.082%
|  | Lightnimg |  | 1 | 1 | Lightnimg |  | 1 | 1 | 0% | 6.25% | 2.041%
|  | Other Contact | 1 |  | 1 | Other Contact | 1 |  | 1 | 3.03% | 0% | 2.041%
|  | Splice | 1 |  | 1 | Splice | 1 |  | 1 | 3.03% | 0% | 2.041%
|  | Switch | 1 |  | 1 | Switch | 1 |  | 1 | 3.03% | 0% | 2.041%
|  | Transformer | 1 | 1 | 2 | Transformer | 1 | 1 | 2 | 3.03% | 6.25% | 4.082%
|  | Vegetation | 4 | 2 | 6 | Vegetation | 4 | 2 | 6 | 12.12% | 12.5% | 12.24%
|  | Vehicle | 4 | 2 | 6 | Vehicle | 4 | 2 | 6 | 12.12% | 12.5% | 12.24%
|  | Wire-to-Wire | 1 |  | 1 | Wire-to-Wire | 1 |  | 1 | 3.03% | 0% | 2.041%
|  | Grand Total | 33 | 16 | 49 | Grand Total | 33 | 16 | 49 | 100% | 100% | 100%

## SCE_Ignition_Lines_24
OBJECTID_12 | OBJECTID | IgnitionID | UtilityID | SubstationID | NearestWeatherStationID | OutageID | FireStartDateTime | FireStartYear | FireDetectionMethod | FireDetectionMethodComment | SuspectedInitiatingCause | SuspectedInitiatingCauseComment | ObjectContact | ObjectContactComment | VegetationGenus | VegetationSpecies | VegetationCommonName | EquipmentFailure | EquipmentFailureComment | AssociatedNominalVoltagekV | AssociatedOperatingVoltagekV | EquipmentType | Determination | DeterminationComment | FacilityContacted | FacilityContactedComment | AssetID | AssetFeature | SegmentID | CircuitID | LineClass | ContributingFactor | ContributingFactorComment | RFWStatus | RFWIssueDateTime | FWWStatus | FWWIssueDateTime | HWWStatus | HWWIssueDateTime | OriginLandUse | MaterialAtOrigin | MaterialAtOriginComment | FuelBedDescription | FuelBedDescriptionComment | FireSize | SuppressedBy | SuppressingAgency | FireInvestigation | FireAHJ | IgnitionNotes | HFTDClass | OBJECTID_1 | SegmentID_1 | CircuitID_1 | UtilityID_1 | SubstationID_1 | CircuitName | ConductorType | ConductorTypeComment | AssetOHUG | NominalVoltagekV | OperatingVoltagekV | SubstationName | ConductorMaterial | ConductorMaterialComment | ConductorSize | ConductorOD | LastInspectionDate | LastMaintenanceDate | InstallationDate | InstallationYear | EstimatedAge | UsefulLifespan | AmpacityRating | OverallUtilityRisk | IgnitionRisk | PSPSRisk | Distance | Reportable | Reported
3 | 5 | FIPA_2024_0303_2336 | SCE | ES-5560 | SCE-3072 |  | 2024-03-04 07:36 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Support structure |  | OH-1790725E | Support Structure |  | ED-15737 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Other, see comment | Car | Fire-resistive fuel bed |  | <0.25 | Fire agency | Los Angeles County FD | No |  |  | Tier 3 | 801917 | 309636716 | ED-15737 | SCE | ES-5560 | SAND CANYON | Covered |  | Overhead | 16 |  | Solemint | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 2022-05-20 | 2022 | 0-9 |  |  | 3.6e-06 | 3.42e-06 | 1.84e-07 | 3.1666 | 1 | 1
1 | 7 | FIPA_2024_0309_0614 | SCE | ES-8096 | SCE-2119 |  | 2024-03-09 14:14 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | OH-83182E | Support Structure |  | ED-15986 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Structure |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Local FD | No |  |  | Tier 3 | 522569 | 84008346 |  | SCE |  |  | Other, see comment |  | Overhead |  |  |  | Other, see comment | [13 empty] | 3.2665 | 1 | 1
2 | 8 | FIPA_2024_0310_2232 | SCE | ED-8318 | SCE-2175 | 130320952 | 2024-03-11 05:32 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Anchor/guy |  | 12 | 12 | Overhead | Utility personnel |  |  |  | OH-2341991E | Support Structure |  | ED-03519 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino FD | No |  |  | Tier 2 | 640311 | 81977481 | ED-03519 | SCE | ED-8318 | CIRCLE | Other, see comment | A | Overhead | 12 |  | OAK SPRINGS P.T. | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 0.0016642 | 0.0016642 | 0 | 2.9864 | 1 | 1
6 | 1 | FIPA_2024_0405_0840 | SCE | ED-7549 | SCE-3296 | 130468727 | 2024-04-05 08:40 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-12178 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Structure |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino County Fire Dep | No |  |  | Tier 2 | 865487 | 335229954 | ED-12178 | SCE | ED-7549 | MORONGO | Other, see comment | A | Overhead | 12 |  | MORONGO P.T. | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2022-03-07 | 2022 | 0-9 |  |  | 0.0015603 | 0.0015602 | 6.15e-08 | 3.0451 | 1 | 1
10 | 19 | FIPA_2024_0415_0320 | SCE | ES-5372 | SCE-2185 | 130506014 | 2024-04-15 03:20 | 2024 | Utility staff |  | Object contact |  | Other, see comment | Inconclusive | [5 empty] | 16 | 16 | Overhead | Utility personnel |  | Conductor: Primary |  | 4743368E-205664653 | Support Structure |  | ED-12011 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 1045279 | 10516129 | ED-12011 | SCE | ES-5372 | MIST | Other, see comment | C | Overhead | 16 |  | Capitan | Other, see comment | C | 2/0 | [11 empty] | 2.5511 | FALSE | 1
4 | 2 | FIPA_2024_0504_0858 | SCE | ES-5380 | SCE-3331 | 130598297 | 2024-05-04 08:58 | 2024 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Transformer |  | 0 | Support Structure |  | ED-17529 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Tier 3 | 215897 | 312056952 | ED-17529 | SCE | ES-5380 | TANAGER | Covered |  | Overhead | 12 |  | BANDUCCI | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-11-01 | 2019 | 0-9 |  |  | 0.00022035 | 0.00022035 | 0 | 1.1192 | FALSE | 1
5 | 28 | FIPA_2024_0516_0930 | SCE | ES-5365 | SCE-3323 |  | 2024-05-16 09:30 | 2024 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Transformer |  | 0 | Support Structure |  | ED-01954 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Utility |  | No |  |  | Tier 3 | 708585 | 312787117 | ED-01954 | SCE | ES-5365 | BOOTLEGGER | Covered |  | Overhead | 12 |  | Acton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 0.0011493 | 0.0011493 | 4.96e-08 | 3.0681 | 1 | 1
8 | 8 | FIPA_2024_0523_1413 | SCE | ES-5536 | SCE-2027 |  | 2024-05-23 14:13 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Fuse |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-14645 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Tier 3 | 910663 | 10493193 | ED-14645 | SCE | ES-5536 | RAINBOW | Covered |  | Overhead | 16 |  | Somis | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-06-02 | 2021 | 0-9 |  |  | 8.98e-07 | 8.8e-07 | 1.78e-08 | 2.5569 | FALSE | 1
7 | 25 | FIPA_2024_0529_1724 | SCE | ES-8306 | SCE-2970 | 130755492 | 2024-05-29 17:24 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-21194 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 875988 | 88589744 | ED-21194 | SCE | ES-8306 | VENWIND 4 | Other, see comment | A | Overhead | 12 |  | Venwind | Aluminum conductor steel reinforced (ACSR) |  | 653 | [9 empty] | 0.00078189 |  | 3.0805 | FALSE | 1
11 | 9 | FIPA_2024_0604_1433 | SCE | ES-5512 | SCE-3479 |  | 2024-06-04 14:33 | 2024 | Fire agency |  | Vandalism/theft | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-09777 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | U.S. Forest Service | No |  |  | Tier 2 | 1156434 | 10531368 | ED-09777 | SCE | ES-5512 | KINSEY | Covered |  | Overhead | 12 |  | Gorman | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 0.00037966 | 0.00037827 | 1.39e-06 | 3.2053 | 1 | 0
9 | 5 | FIPA_2024_0626_0715 | SCE |  | SCE-2571 |  | 2024-06-26 07:15 | 2024 |  |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Splice/clamp/connector |  | 0 | Support Structure |  |  | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban |  |  | Other, see comment | Minor Roads surrounded by Low FB fuel | <3 meters of linear travel | Fire agency | KERN COUNTY FD_NONE | No |  |  | Tier 3 | 947032 | 73692637 | ED-02680 | SCE | ES-5357 | CALIENTE | Other, see comment | A | Overhead | 12 |  | Cummings | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2022-08-11 | 2022 | 0-9 |  |  | 3.76e-06 | 3.76e-06 | 0 | 3.1908 | FALSE | 0
14 | 8 | FIPA_2024_0707_1515 | SCE | ES-5570 | SCE-3076 |  | 2024-07-07 15:15 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Pole |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 1286521E-201831050 | Support Structure |  | ED-17605 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Santa Barbara Fire Department | No |  |  | Tier 3 | 192850 | 10521047 | ED-17605 | SCE | ES-5570 | TECOLOTE | Other, see comment | A | Overhead | 16 |  | Vegas | Aluminum conductor steel reinforced (ACSR) |  | 4 | [9 empty] | 4.75e-05 |  | 3.0784 | FALSE | 0
26 | 44 | FIPA_2024_0710_0011 | SCE | ES-5115 | SCE-2648 |  | 2024-07-10 00:11 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Splice |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 4614792E-202006041 | Support Structure |  | ED-10020 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 674629 | 133930338 | ED-10020 | SCE | ES-5115 | LAMANDA | Other, see comment | A | Overhead | 16 |  | Eaton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 0.00049545 | 0.00049545 | 0 | 3.0465 | 1 | 0
18 | 50 | FIPA_2024_0710_1059 | SCE | ES-8056 | SCE-2327 |  | 2024-07-10 10:59 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-19586 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 380105 | 337674503 | ED-19586 | SCE | ES-8056 | WOBEGONE | Covered |  | Overhead | 12 |  | LAKEVIEW | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-11-29 | 2021 | 0-9 |  |  | 0.0035158 | 0.0035158 | 0 | 3.1634 | 1 | 0
17 | 21 | FIPA_2024_0718_1136 | SCE | ES-5526 | SCE-3288 | 131007759 | 2024-07-18 11:36 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 4863233E-207633728 | Support Structure |  | ED-17731 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 379425 | 309085482 | ED-17731 | SCE | ES-5526 | THACHER | Covered |  | Overhead | 16 |  | Ojai | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-01-01 | 2019 | 0-9 |  |  | 4.86e-05 | 4.86e-05 | 0 | 2.9043 | 1 | 1
15 | 27 | FIPA_2024_0718_2252 | SCE | ES-5365 | SCE-2245 | 131009037 | 2024-07-18 22:52 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | 4429426E-205706899 | Support Structure |  | ED-14047 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 276998 | 312913703 | ED-14047 | SCE | ES-5365 | PICK | Covered |  | Overhead | 12 |  | Acton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-05-16 | 2021 | 0-9 |  |  | 0.0035664 | 0.0035664 | 2.71e-09 | 3.0474 | FALSE | 1
23 | 51 | FIPA_2024_0723_1526 | SCE | ES-5351 | SCE-2286 | 131032058 | 2024-07-23 15:26 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | 0 | Support Structure |  | ED-05850 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Tulare County Fire Department | No |  |  | Tier 2 | 601797 | 67614993 | ED-05850 | SCE | ES-5351 | ELSTER | Other, see comment | C | Overhead | 12 |  | Boxwood | Other, see comment | C | 6 | [11 empty] | 3.0483 | FALSE | 1
19 | 10 | FIPA_2024_0724_1320 | SCE | ES-8342 | SCE-3350 |  | 2024-07-24 13:20 | 2024 | Public |  | Equipment failure | [6 empty] | Splice |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 4978055E-250029539 | Support Structure |  | ED-11058 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Customer |  | No |  |  | Tier 2 | 454490 | 344422477 | ED-11058 | SCE | ES-8342 | MENIFEE | Covered |  | Overhead | 12 |  | Newcomb | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 2022-09-14 | 2022 | 0-9 |  |  |  | 2.14e-06 |  | 3.122 | 1 | 0
20 | 22 | FIPA_2024_0727_1933 | SCE | ES-5508 | SCE-3480 | 131054013 | 2024-07-27 19:33 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Transformer |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 709052E-208285916 | Support Structure |  | ED-08810 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 506736 | 10553284 | ED-08810 | SCE | ES-5508 | HUGHES LAKE | Covered |  | Overhead | 12 |  | Del Sur | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 0.0021475 | 0.0021475 | 1.81e-09 | 2.8434 | 1 | 1
24 | 28 | FIPA_2024_0728_1243 | SCE | ES-5070 | SCE-2752 |  | 2024-07-28 12:43 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Conductor: Primary |  | 312510S-200821631 | Support Structure |  | ED-06504 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 630765 | 120266107 | ED-06504 | SCE | ES-5070 | ROS | Other, see comment | A | Overhead | 12 |  | Valley | Aluminum conductor steel reinforced (ACSR) |  | 336 | [8 empty] | 0.00045621 | 0.00043823 | 1.8e-05 | 5.1484 | 1 | 1
13 | 40 | FIPA_2024_0730_0000 | SCE | ES-5569 | SCE-2142 |  | 2024-07-30 | 2024 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-04226 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 120387 | 346302433 | ED-04226 | SCE | ES-5569 | COVENTRY | Other, see comment | A | Overhead | 16 |  | Thousand Oaks | Aluminum conductor steel reinforced (ACSR) |  | 4/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 0.0062664 | 0.0062631 | 3.33e-06 | 7.1992 | 1 | 1
12 | 52 | FIPA_2024_0731_1330 | SCE | ES-8010 | SCE-2599 | 131067902 | 2024-07-31 13:30 | 2024 | Utility staff |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Fuse |  | 0 | Support Structure |  | ED-10735 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 102277 | 81988088 | ED-10735 | SCE | ES-8010 | LOTTO | Covered |  | Overhead | 12 |  | Phelan | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [9 empty] | 0.0012501 |  | 3.2453 | FALSE | 1
28 | 58 | FIPA_2024_0801_1458 | SCE | EX-4135 | SCE-2441 |  | 2024-08-01 14:58 | 2024 | Fire agency |  | Wire-to-wire contact | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 851612E-201781968 | Support Structure |  | ED-04540 | Secondary Distribution Line |  |  | Yes | 2024-08-01 19:00 | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Ventura County Fire Department | No |  |  | Tier 2 | 754113 | 345416467 | ED-04540 | SCE | EX-4135 | CUYAMA | Other, see comment | UNKNOWN | Overhead | 12 |  | TAFT | Other, see comment | UNKNOWN | UNKNOWN |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 5.17e-05 | 5.17e-05 | 0 | 3.2464 | 1 | 1
27 | 41 | FIPA_2024_0815_0853_1 | SCE | ES-5067 | SCE-2328 | 131146427 | 2024-08-15 08:53 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Insulator |  | 0 | Support Structure |  | ED-08946 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 734827 | 88589662 | ED-08946 | SCE | ES-5067 | INVADER | Other, see comment | A | Overhead | 12 |  | Devers | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 0.00040384 | 0.00040211 | 1.73e-06 | 3.0061 | 1 | 1
22 | 59 | FIPA_2024_0818_1730 | SCE | ES-5546 | SCE-3735 |  | 2024-08-18 17:30 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Insulator |  | 589097E-208564453 | Support Structure |  | ED-07742 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 554524 | 347344868 | ED-00484 | SCE | ES-5542 | ANACONDA | Other, see comment | A | Overhead | 16 |  | North Oaks | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ | [5 empty] | 49085.8139 | 1 | 1
25 | 18 | FIPA_2024_0823_0440 | SCE | ES-5372 | SCE-2318 |  | 2024-08-23 04:40 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 807731E-201916856 | Support Structure |  | ED-12011 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 10-99 | Fire agency | Santa Barbara County Fire Depa | No |  |  | Tier 3 | 667562 | 10524446 | ED-17605 | SCE | ES-5570 | TECOLOTE | Other, see comment | A | Overhead | 16 |  | Vegas | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 0.00011683 | 0.00011683 | 0 | 72800.2021 | 1 | 0
21 | 48 | FIPA_2024_0827_1411 | SCE | ES-5542 | SCE-2561 | 131197570 | 2024-08-27 14:11 | 2024 | Fire agency |  | Equipment failure | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 4081329E-202213667 | Support Structure |  | ED-00484 | Primary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 554524 | 347344868 | ED-00484 | SCE | ES-5542 | ANACONDA | Other, see comment | A | Overhead | 16 |  | North Oaks | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ | [5 empty] | 7.2518 | 1 | 1
16 | 54 | FIPA_2024_0829_1239 | SCE | ES-5275 | SCE-2801 |  | 2024-08-29 12:39 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-12161 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 2 | 372778 | 218689685 | ED-12161 | SCE | ES-5275 | SHORELINE | Other, see comment | C | Overhead | 16 |  | Marymount | Other, see comment | C | 6 | [9 empty] | 0.00052467 |  | 3.1127 | FALSE | 1
33 | 7 | FIPA_2024_1010_1329 | SCE | ES-5661 | SCE-2481 |  | 2024-10-10 13:29 | 2024 | Utility staff |  | Lightning | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 1763305E-206910933 | Support Structure |  | ED-17475 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 3 | 948985 | 70865521 | ED-17475 | SCE | ES-5661 | TAGGERT | Covered |  | Overhead | 12 |  | RUNNING SPRINGS | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 0.00084054 | 0.00084041 | 1.3098 | 3.3183 | FALSE | 1
29 | 18 | FIPA_2024_1024_1529 | SCE | ES-5015 | SCE-2646 |  | 2024-10-24 15:29 | 2024 | Public |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-19694 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 2 | 55941 | 133940812 | ED-19694 | SCE | ES-5015 | ANGELES | Other, see comment | A | Overhead | 16 |  | GOULD | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 1.3206 | 1.2924 | 2.8242 | 5.2458 | 1 | 0
32 | 11 | FIPA_2024_1106_0830 | SCE | ES-5580 | SCE-2353 |  | 2024-11-06 08:30 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 1584827E-201856148 | Support Structure |  | ED-08707 | Secondary Distribution Line | Weather |  | Yes | 2024-11-06 10:00 | No |  | Yes | 2024-11-06 10:00 | Urban | Vegetation |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 857453 | 303514935 | ED-08707 | SCE | ES-5580 | HOSS | Other, see comment | A | Overhead | 16 |  | ROYAL | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 0.00049433 | 0.00048595 | 8.3731 | 77.71 | 1 | 0
31 | 15 | FIPA_2024_1109_1544 | SCE | ED-7657 | SCE-2679 |  | 2024-11-09 15:44 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 356425S-201298179 | Support Structure |  | ED-14005 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 3 | 821626 | 84010534 | ED-14005 | SCE | ED-7657 | PHEASANT | Covered |  | Overhead | 12 |  | PHEASANT P.T. | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-07-20 | 2021 | 0-9 |  |  | 0.080209 | 0.080209 | 1.7895 | 6.0709 | 1 | 0
30 | 6 | FIPA_2024_1201_0933 | SCE | ES-5576 | SCE-2223 |  | 2024-12-01 09:33 | 2024 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Other, see comment | Lightning Arrester | 0 | Support Structure |  | ED-02674 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 186173 | 10556305 | ED-02674 | SCE | ES-5576 | CALGROVE | Covered |  | Overhead | 16 |  | NEWHALL | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ | [5 empty] | 3.1676 | FALSE | 1

## SCE_Ignition_Lines_23
OBJECTID_12 | OBJECTID | IgnitionID | UtilityID | SubstationID | NearestWeatherStationID | OutageID | OutageStatus | FireStartDateTime | FireStartYear | FireDetectionMethod | FireDetectionMethodComment | SuspectedInitiatingCause | SuspectedInitiatingCauseComment | ObjectContact | ObjectContactComment | VegetationGenus | VegetationSpecies | VegetationCommonName | EquipmentFailure | EquipmentFailureComment | AssociatedNominalVoltagekV | AssociatedOperatingVoltagekV | OtherCompanies | EquipmentType | Determination | DeterminationComment | FacilityContacted | FacilityContactedComment | AssetID | AssetFeature | SegmentID | CircuitID | LineClass | ContributingFactor | ContributingFactorComment | RFWStatus | RFWIssueDateTime | FWWStatus | FWWIssueDateTime | HWWStatus | HWWIssueDateTime | OriginLandUse | MaterialAtOrigin | MaterialAtOriginComment | FuelBedDescription | FuelBedDescriptionComment | FireSize | SuppressedBy | SuppressingAgency | FireInvestigation | FireAHJ | IgnitionNotes | HFTDClass | Latitude | Longitude | OBJECTID_1 | SegmentID_1 | CircuitID_1 | UtilityID_1 | SubstationID_1 | CircuitName | ConductorType | ConductorTypeComment | AssetOHUG | NominalVoltagekV | OperatingVoltagekV | SubstationName | ConductorMaterial | ConductorMaterialComment | ConductorSize | ConductorOD | LastInspectionDate | LastMaintenanceDate | InstallationDate | InstallationYear | EstimatedAge | UsefulLifespan | AmpacityRating | Greased | OverallUtilityRisk | IgnitionRisk | PSPSRisk | Distance | GE_FID
1 | 2 | FIPA_2023_0214_2129 | SCE | ES-5853 | SCE-3048 | 128407122 | Yes | 2023-02-14 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-1805980E | Support Structure |  | ED-13734 | Primary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Other, see comment | Shrubs and mulch, landscaping | <3 meters of linear travel | Fire agency | Local FD | No |  |  | Non-HFTD | 33.7099 | -117.9324 | 236096 | 197198307 | ED-13734 | SCE | ES-5853 | PARROT | Other, see comment | A | Overhead | 12 | -99 | Talbert | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0748
2 | 1 | FIPA_2023_0114_2218 | SCE | ES-5886 | SCE-2976 | 128261538 | Yes | 2023-01-14 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Ailanthus | Altissima | Ailanthus |  |  | 12 | 12 | Frontier | Overhead | Utility personnel |  | Conductor: Primary |  | OH-977927E | Support Structure |  | ED-13653 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | LACFD | No |  |  | Non-HFTD | 33.9193 | -118.0784 | 256660 | 217885006 | ED-13653 | SCE | ES-5886 | PAPOOSE | Other, see comment | A | Overhead | 12 | -99 | Pioneer | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2329
3 | 3 | FIPA_2023_0224_0641 | SCE | ES-5331 | SCE-2133 | 128463887 | Yes | 2023-02-24 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Insulator and bushing |  | 12 | 12 | AT&T California | Overhead | Utility personnel |  |  |  | OH-1757703E | Support Structure |  | ED-17590 | Primary Distribution Line |  |  | No |  | No |  | No |  | Urban | Other, see comment | Motor Vehicle | Fire-resistive fuel bed |  | <3 meters of linear travel | Fire agency | Visalia Fire Department | No |  |  | Non-HFTD | 36.3202 | -119.294 | 560756 | 67611629 | ED-17590 | SCE | ES-5331 | TAYLOR | Bare |  | Overhead | 12 | -99 | Visalia | Other, see comment | Unknown | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.9644
4 | 4 | FIPA_2023_0226_1605 | SCE | ES-8227 | SCE-2592 | 128504283 | Yes | 2023-02-26 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Insulator and bushing |  | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-1992363E | Support Structure |  | ED-05636 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Riverside County Fire | No |  |  | Non-HFTD | 33.5824 | -114.6919 | 756277 | 73748427 | ED-05636 | SCE | ES-8227 | EIGHTEENTH | Other, see comment | C | Overhead | 12 | -99 | Ripley | Other, see comment | C | 6 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.9877
5 | 6 | FIPA_2023_0609_2119 | SCE | ES-5504 | SCE-2809 | 129018104 | Yes | 2023-06-10 04:19 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Connector device |  | 16 | 16 | NA | Overhead | Utility personnel |  |  |  | OH-4204614E | Support Structure |  | ED-15828 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Ventura County FD | No |  |  | Tier 3 | 34.3194 | -119.2905 | 31369 | 10509836 | ED-02860 | SCE | ES-5504 | CANET | Other, see comment | A | Overhead | 16 | -99 | Casitas | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown | 0.00001587 | 0.00001549 | 0.00000037 | 3.0889
6 | 13 | FIPA_2023_0513_1639 | SCE | ES-5021 | SCE-2796 | 128890731 | Yes | 2023-05-13 23:39 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Lightning arrester |  | 16 | 16 | NA | Overhead | Utility personnel |  |  |  | OH-1319282E | Support Structure |  | ED-14480 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  |  | Non-HFTD | 33.8676 | -118.3352 | 67491 | 337518442 | ED-14480 | SCE | ES-5021 | PUEBLO | Other, see comment | C | Overhead | 16 | -99 | La Fresa | Other, see comment | C | 4/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 4.9264
7 | 14 | FIPA_2023_0522_1538 | SCE | ES-5136 | SCE-2972 |  | No | 2023-05-22 22:38 | 2023 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 16 | 16 | AT&T California, Crown Castle NG West | Overhead | Utility personnel |  | Conductor: Primary |  | OH-4435916E | Support Structure |  | ED-08303 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Other, see comment | Shrubs and mulch, landscaping | <0.25 | Fire agency | Local FD | No |  |  | Non-HFTD | 34.0425 | -118.143 | 192334 | 133979519 | ED-08303 | SCE | ES-5136 | HELM | Other, see comment | A | Overhead | 16 | -99 | Newmark | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0133
8 | 5 | FIPA_2023_0428_1216 | SCE | ES-8049 | SCE-2884 | 128828523 | Yes | 2023-04-28 19:16 | 2023 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | NA | Overhead | Utility personnel |  | Conductor: Primary |  | OH-1756806E | Support Structure |  | ED-00814 | Primary Distribution Line | Human Error |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Victorville FD | No |  |  | Non-HFTD | 34.514 | -117.3814 | 483740 | 81942341 | ED-19870 | SCE | ES-8049 | ZUNI | Other, see comment | A | Overhead | 33 | -99 | Victor | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2607
9 | 11 | FIPA_2023_0512_1830 | SCE | ES-5511 | SCE-2473 | 128887878 | Yes | 2023-05-13 01:30 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | AT&T California | Overhead | Utility personnel |  |  |  | OH-1986855E | Support Structure |  | ED-02048 | Secondary Distribution Line | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Unknown |  | No |  |  | Non-HFTD | 35.0665 | -118.1825 | 512650 | 73687782 | ED-02048 | SCE | ES-5511 | BOXCAR | Other, see comment | A | Overhead | 12 | -99 | Goldtown | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2609
10 | 12 | FIPA_2023_0513_0918 | SCE | ES-5548 | SCE-2831 | 128889128 | Yes | 2023-05-13 16:18 | 2023 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | NA | Overhead | Utility personnel |  | Support structure |  | OH-457620E | Support Structure |  | ED-17963 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Fire agency | LA County FD | No |  |  | Non-HFTD | 34.6754 | -118.0722 | 525876 | 10550894 |  | SCE |  |  | Other, see comment |  | Overhead |  | -99 |  | Other, see comment | [7 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2077
11 | 10 | FIPA_2023_0508_0833 | SCE | ES-8049 | SCE-2641 |  | No | 2023-05-08 15:33 | 2023 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 33 | 33 | NA | Overhead | Utility personnel |  | Other, see comment | Sectionalizer | OH-4877541E | Support Structure |  | ED-01424 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Non-HFTD | 34.5927 | -117.3256 | 533146 | 341477063 | ED-01424 | SCE | ES-8049 | BURNETTA | Other, see comment | A | Overhead | 33 | -99 | Victor | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0598
12 | 2 | FIPA_2023_0606_1128 | SCE | ES-8137 | SCE-2279 | 129000346 | Yes | 2023-06-06 18:28 | 2023 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | NA | Overhead | Utility personnel |  | Support structure |  | OH-2056033E | Support Structure |  | ED-04784 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Other, see comment | Transformer oil | Fire-resistive fuel bed |  | <0.25 | Fire agency | Kern County Fire Department | No |  |  | Non-HFTD | 35.648 | -117.6914 | 537279 | 73737370 | ED-04784 | SCE | ES-8137 | DEETER | Other, see comment | A | Overhead | 12 | -99 | Downs | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2081
13 | 4 | FIPA_2023_0607_1659 | SCE | ES-5041 | SCE-2279 | 129005011 | Yes | 2023-06-07 23:59 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Frontier Communications | Overhead | Utility personnel |  | Transformer |  | OH-2110153E | Support Structure |  | ED-08423 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Unknown | Kern County Fire Department | No |  |  | Non-HFTD | 35.7491 | -117.8558 | 538027 | 73734342 | ED-08423 | SCE | ES-5041 | HIGHWAY SIX | Other, see comment | A | Overhead | 12 | -99 | Inyokern | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0123
14 | 8 | FIPA_2023_0616_1127 | SCE | ES-5328 | SCE-2133 | 129045355 | Yes | 2023-06-16 18:27 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Lightning arrester |  | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-2321438E | Support Structure |  | ED-03170 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Other, see comment | Timber pile and dry grass | <0.25 | Fire agency | Tulare County Fire | No |  |  | Non-HFTD | 36.2122 | -119.2803 | 582392 | 67644224 | ED-03170 | SCE | ES-5328 | CATTLE | Other, see comment | A | Overhead | 12 | -99 | Tulare | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.1558
15 | 9 | FIPA_2023_0508_0248 | SCE | ES-5619 | SCE-2846 |  | No | 2023-05-08 09:48 | 2023 | Fire agency |  | Vandalism/theft | [8 empty] | 12 | 12 | AT&T California | Overhead | Utility personnel |  |  |  | OH-2357048E | Support Structure |  | ED-16730 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  |  | Non-HFTD | 34.1129 | -117.2252 | 634077 | 120265038 | ED-06985 | SCE | ES-8024 | GAMBLE | Other, see comment | A | Overhead | 12 | -99 | Alessandro | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 80848.9365
16 | 3 | FIPA_2023_0425_0849 | SCE | ES-8024 | SCE-3011 |  | No | 2023-04-25 15:49 | 2023 | Utility staff |  | Vandalism/theft | [8 empty] | 12 | 12 | Frontier Communications | Overhead | Utility personnel |  |  |  | OH-2173288E | Support Structure |  | ED-06985 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Non-HFTD | 33.8897 | -117.2305 | 634147 | 120268105 | ED-06985 | SCE | ES-8024 | GAMBLE | Other, see comment | A | Overhead | 12 | -99 | Alessandro | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0091
17 | 7 | FIPA_2023_0507_1358 | SCE | ES-8260 | SCE-2641 | 128865914 | Yes | 2023-05-07 20:58 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 33 | 33 | NA | Overhead | Utility personnel |  | Other, see comment | Lightning Arrester | OH-81314S | Support Structure |  | ED-16124 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Apple Valley Fire Department | No |  |  | Non-HFTD | 34.532 | -117.2796 | 700686 | 252490925 | ED-16124 | SCE | ES-8260 | SENECA | Other, see comment | A | Overhead | 33 | -99 | Victorville | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0707
18 | 1 | FIPA_2023_0403_1658 | SCE | ES-8222 | SCE-2641 | 128716701 | Yes | 2023-04-03 23:58 | 2023 | Other, see comment | Police Department | Equipment failure | [6 empty] | Insulator and bushing |  | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-3006101E | Support Structure |  | ED-09828 | Primary Distribution Line | Unknown |  | No |  | No |  | Yes | 2023-04-03 12:00 | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Unknown |  | No |  |  | Non-HFTD | 34.5475 | -117.2171 | 703714 | 81952826 | ED-09828 | SCE | ES-8222 | KNOLLS | Other, see comment | A | Overhead | 12 | -99 | Rancho | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.983
19 | 16 | FIPA_2023_0707_1344 | SCE | ES-0157 | SCE-2934 | 129142217 | Yes | 2023-07-07 20:44 | 2023 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Frontier | Overhead | Utility personnel |  | Switch |  | OH-2224882E | Support Structure |  | ED-18229 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Unknown |  | No |  |  | Non-HFTD | 33.7428 | -117.1648 | 195076 | 120273050 | ED-04723 | SCE | ES-5070 | DEACON | Other, see comment | A | Overhead | 12 | -99 | Valley | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.965 | 965631787
20 | 17 | FIPA_2023_0726_0252 | SCE | ES-8260 | SCE-2641 |  | No | 2023-07-26 09:52 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | NA | Subsurface | Utility personnel |  |  |  | UG-5588536 | Support Structure |  | ED-09469 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <3 meters of linear travel | Fire agency | Local FD | No |  |  | Non-HFTD | 34.548 | -117.2805 | 198388 | 315589801 | ED-18674 | SCE | ES-8042 | VERDEMONT | Other, see comment | UNKNOWN | Overhead | 33 | -99 | Calectric | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown | 1.311E-05 | 9.24E-06 | 3.86E-06 | 125273.3286 | 965795000
21 | 19 | FIPA_2023_0804_1139 | SCE | ES-8093 | SCE-2267 |  | No | 2023-08-04 18:39 | 2023 | Public |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | NA | Subsurface | Utility personnel |  |  |  | OH-4923136E | Support Structure |  | ED-12847 | Secondary Distribution Line | Human Error |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Fire agency | Local FD | No |  |  | Tier 2 | 34.2141 | -117.3939 | 198388 | 315589801 | ED-18674 | SCE | ES-8042 | VERDEMONT | Other, see comment | UNKNOWN | Overhead | 33 | -99 | Calectric | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown | 1.311E-05 | 9.24E-06 | 3.86E-06 | 3.064 | 965795000
22 | 13 | FIPA_2023_0723_0951 | SCE | ES-5070 | SCE-3081 | 129217433 | Yes | 2023-07-23 16:51 | 2023 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | NA | Overhead | Utility personnel |  | Conductor: Primary |  | OH-4269395E | Support Structure |  | ED-12482 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire | No |  |  | Non-HFTD | 33.7509 | -117.1827 | 238363 | 120273097 | ED-12482 | SCE | ES-5070 | NAPA | Other, see comment | A | Overhead | 12 | -99 | Valley | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.1917 | 965631889
23 | 23 | FIPA_2023_0808_0521 | SCE | ES-5577 | SCE-2869 | 129310056 | Yes | 2023-08-08 12:21 | 2023 | Fire agency |  | Contamination | [8 empty] | 16 | 16 | NA | Overhead | Utility personnel |  |  |  | OH-1643591E | Support Structure |  | ED-13885 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Ventura County FD | Yes, complete |  |  | Non-HFTD | 34.2432 | -119.2474 | 273220 | 10493401 | ED-13885 | SCE | ES-5577 | PEDRO | Bare |  | Overhead | 16 | -99 | San Miguel | Other, see comment | Unknown | 2 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 5.3416 | 965190038
24 | 18 | FIPA_2023_0708_0000 | SCE | ES-5188 | SCE-3002 |  | No | 2023-07-08 07:00 | 2023 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Frontier | Overhead | Utility personnel |  | Conductor: Primary |  | OH-1942404E | Support Structure |  | ED-04630 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Other, see comment | VEGETATION and PLANTS | <3 meters of linear travel | Fire agency |  | No |  |  | Non-HFTD | 34.0949 | -117.9014 | 312152 | 147463586 | ED-04630 | SCE | ES-5188 | DAMERAL | Other, see comment | A | Overhead | 12 | -99 | Dalton | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.026 | 965354962
25 | 4 | FIPA_2023_0703_1935 | SCE | ES-8016 | SCE-2691 | 129129206 | Yes | 2023-07-04 02:35 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | Frontier | Overhead | Utility personnel |  |  |  | OH-4627868E | Support Structure |  | ED-06361 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Other, see comment | Riser | Other, see comment | PVC | <3 meters of linear travel | Self-extinguished |  | No |  |  | Non-HFTD | 33.8508 | -116.5275 | 341974 | 88594106 | ED-06361 | SCE | ES-8016 | FEY | Other, see comment | A | Overhead | 12 | -99 | Farrell | Aluminum conductor steel reinforced (ACSR) |  | 2 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0814 | 965325657
26 | 12 | FIPA_2023_0705_0856 | SCE | ES-5522 | SCE-2573 | 129132941 | Yes | 2023-07-05 15:56 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Frontier | Overhead | Utility personnel |  | Transformer |  | OH-2038927E | Support Structure |  | ED-05928 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Other, see comment | grass and structure | 0.26-9.99 | Fire agency | LA County FD | No |  |  | Non-HFTD | 34.6471 | -118.1699 | 451080 | 10551485 | ED-05928 | SCE | ES-5522 | ENDOR | Other, see comment | C | Overhead | 12 | -99 | Shuttle | Other, see comment | C | 6 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.1737 | 965319349
27 | 3 | FIPA_2023_0808_1253 | SCE | ES-5619 | SCE-3047 |  | No | 2023-08-08 19:53 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | AT&T California | Overhead | Utility personnel |  | Conductor: Secondary |  | OH-225116E | Support Structure |  | ED-12900 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Structure |  | Fire-resistive fuel bed |  | <3 meters of linear travel | Fire agency | Local FD | No |  |  | Non-HFTD | 34.118 | -117.2205 | 523925 | 328352076 | ED-12900 | SCE | ES-5619 | NORWOOD | Other, see comment | A | Overhead | 12 | -99 | Highland | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-03-06 | 2019 | 0-9 | -99 |  | Unknown |  |  |  | 3.2443 | 965819176
28 | 5 | FIPA_2023_0715_1148 | SCE | ES-5050 | SCE-2216 |  | No | 2023-07-15 18:48 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 220 | 220 | NA | Overhead | Utility personnel |  |  |  | OH-7022774 | Support Structure |  | ET-00667 | Transmission Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Local FD | No |  |  | Tier 3 | 34.5541 | -118.6655 | 583011 | 10483309 | ED-03601 | SCE | ES-5546 | CLARINET | Other, see comment | A | Overhead | 16 | -99 | Elizabeth Lake | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown | 0.00189411 | 0.00189404 | 6E-08 | 1252.8851 | 965222238
29 | 8 | FIPA_2023_0716_0103 | SCE | ES-5546 | SCE-2216 | 129184852 | Yes | 2023-07-16 08:03 | 2023 | Fire agency |  | Wire-to-wire contact | [8 empty] | 16 | 16 | NA | Overhead | Utility personnel |  |  |  | OH-1848178E | Support Structure |  | ED-03601 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Local FD | No |  |  | Tier 3 | 34.552 | -118.6621 | 583011 | 10483309 | ED-03601 | SCE | ES-5546 | CLARINET | Other, see comment | A | Overhead | 16 | -99 | Elizabeth Lake | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown | 0.00189411 | 0.00189404 | 6E-08 | 15.6763 | 965222238
30 | 11 | FIPA_2023_0720_1227 | SCE | ES-8342 | SCE-2934 |  | No | 2023-07-20 19:27 | 2023 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | NA | Overhead | Utility personnel |  | Support structure |  | OH-4234514E | Support Structure |  | ED-19001 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Local FD | No |  |  | Non-HFTD | 33.7153 | -117.1827 | 636273 | 120279028 | ED-19001 | SCE | ES-8342 | WARDELL | Other, see comment | A | Overhead | 12 | -99 | Newcomb | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.9746 | 965516125
31 | 7 | FIPA_2023_0703_2112 | SCE | ES-8342 | SCE-3010 | 129127716 | Yes | 2023-07-04 04:12 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | NA | Subsurface | Utility personnel |  |  |  | UG-5536213 | Support Structure |  | ED-08055 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Tier 2 | 33.6843 | -117.2097 | 641097 | 120279032 | ED-19001 | SCE | ES-8342 | WARDELL | Other, see comment | A | Overhead | 12 | -99 | Newcomb | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 13572.2751 | 965516196
32 | 21 | FIPA_2023_0807_1051 | SCE | ES-5566 | SCE-2246 |  | No | 2023-08-07 17:51 | 2023 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Frontier Communications | Overhead | Utility personnel |  | Riser |  | OH-1373589E | Support Structure |  | ED-19243 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Utility |  | No |  |  | Non-HFTD | 34.6292 | -118.2365 | 688465 | 10550566 | ED-19243 | SCE | ES-5566 | WHIP | Other, see comment | A | Overhead | 12 | -99 | Quartz Hill | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0514 | 965565731
33 | 14 | FIPA_2023_0706_1200 | SCE | ES-8038 | SCE-2767 |  | No | 2023-07-06 19:00 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-2178287E | Support Structure |  | ED-01731 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Non-HFTD | 33.7873 | -116.9875 | 750861 | 120277877 | ED-01731 | SCE | ES-8038 | BISSELL | Other, see comment | A | Overhead | 12 | -99 | Nelson | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.1942 | 965381084
34 | 2 | FIPA_2023_0713_2046 | SCE | ES-5648 | SCE-2952 | 129169822 | Yes | 2023-07-14 03:46 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Other, see comment | Pothead | 12 | 12 | NA | Overhead | Utility personnel |  |  |  | OH-779457E | Support Structure |  | ED-00740 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Local FD | No |  |  | Non-HFTD | 34.0473 | -117.6743 | 776303 | 147438385 | ED-01940 | SCE | ES-5648 | BONVIEW | Other, see comment | A | Overhead | 12 | -99 | Narod | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.4426 | 965400353
35 | 6 | FIPA_2023_0815_1656 | SCE | ES-5272 | SCE-2307 | 129328592 | Yes | 2023-08-15 23:56 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Insulator and bushing |  | 16 | 16 | Frontier Communications | Overhead | Utility personnel |  |  |  | OH-1408752E | Support Structure |  | ED-06924 | Secondary Distribution Line | Other, see comment | Corrosion dead-end insulator | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Local FD | No |  |  | Tier 3 | 34.0454 | -118.9351 | 851131 | 307422952 | ED-06924 | SCE | ES-5272 | GALAHAD | Covered |  | Overhead | 16 | -99 | Latigo | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2018-01-01 | 2018 | 0-9 | -99 |  | Unknown | 1.04E-06 | 1.01E-06 | 2E-08 | 2.1328 | 965326747
36 | 1 | FIPA_2023_0703_0951 | SCE | ES-5196 | SCE-3075 | 129125822 | Yes | 2023-07-03 16:51 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | NA | Subsurface | Utility personnel |  |  |  | UG-5163274 | Support Structure |  | ED-18087 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Structure |  | Other, see comment | structure | <3 meters of linear travel | Fire agency | LA County FD | No |  |  | Non-HFTD | 33.9848 | -117.8628 | 894034 | 147464252 | ED-04630 | SCE | ES-5188 | DAMERAL | Other, see comment | A | Overhead | 12 | -99 | Dalton | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 41655.8322 | 965354944
37 | 15 | FIPA_2023_0725_1239 | SCE | ES-8225 | SCE-3068 | 129227678 | Yes | 2023-07-25 19:39 | 2023 | Public |  | Vandalism/theft | [8 empty] | 12 | 12 | NA | Pad-mounted | Utility personnel |  |  |  | ES-8225-0033-XF-2-ABC | Transformer Site |  | ED-05672 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Customer |  | No |  | 3rd party threw object over fence into substation which caused burning debris to start a fire. | Non-HFTD | 34.1013 | -117.3681 | 966676 | 113795791 | ED-06607 | SCE | ES-8042 | FONRI | Other, see comment | UNKNOWN | Overhead | 33 | -99 | Calectric | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 18.2124 | 965869968
38 | 22 | FIPA_2023_0712_1208 | SCE | ES-5053 | SCE-2187 |  | No | 2023-07-12 19:08 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 66 | 66 | NA | Overhead | Utility personnel |  | Other, see comment | Crossarm and weight holding down jumpers | OH-4425342E | Support Structure |  | ET-00436 | Transmission Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Ventura County FD | No |  |  | Tier 3 | 34.4433 | -119.508 | 1038830 | 10492977 | ED-15701 | SCE | ES-5577 | SALVADOR | Other, see comment | C | Overhead | 16 | -99 | San Miguel | Other, see comment | C | 4/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 106674.1688 | 965263248
39 | 10 | FIPA_2023_0705_0124 | SCE | ES-5706 | SCE-2424 |  | No | 2023-07-05 08:24 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Conductor |  | 4 | 4 | Frontier | Overhead | Utility personnel |  |  |  | OH-797595E | Support Structure |  | ED-14710 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Vegetation |  | Other, see comment | fence, side walk and grass | <3 meters of linear travel | Self-extinguished |  | No |  |  | Non-HFTD | 33.7774 | -118.1617 | 1105215 | 217920329 | ED-14710 | SCE | ES-5706 | RANSOM | Other, see comment | UNKNOWN | Overhead | 4 | -99 | Belmont | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0136 | 965585475
40 | 20 | FIPA_2023_0710_0710 | SCE | ES-5835 | SCE-3048 | 129151420 | Yes | 2023-07-10 14:10 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | NA | Subsurface | Utility personnel |  |  |  | UG-5071406 | Support Structure |  | ED-15601 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  |  | Other, see comment | Cable | Other, see comment | side walk and green landscaping | <3 meters of linear travel | Self-extinguished |  | No |  |  | Non-HFTD | 33.7598 | -117.849 | 1119242 | 197168083 | ED-05215 | SCE | ES-5835 | DORIS | Other, see comment | A | Overhead | 12 | -99 | La Veta | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 92.9819 | 965649227
41 | 9 | FIPA_2023_0902_1715 | SCE | ES-5012 | SCE-2972 | 129454855 | Yes | 2023-09-03 00:15 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 16 | 16 | AT&T California | Overhead | Utility personnel |  |  |  | OH-4516571E | Support Structure |  | ED-10665 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Local FD | No |  | Failed pothead riser caused pole fire and small spot fire. | Non-HFTD | 34.0408 | -118.1059 | 1174135 | 290986467 | ED-10665 | SCE | ES-5012 | LOMAS | Other, see comment | A | Overhead | 16 | -99 | Mesa | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 4.8426 | 965747669
42 | 12 | FIPA_2023_1120_2014 | SCE | ES-8021 | SCE-2996 | 129856470 |  | 2023-11-21 04:14 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Bougainvillea | Bougainvillea glabra Choisy | Bougainvillea |  |  | 12 | 12 |  | Overhead | Utility personnel |  | Conductor: Secondary |  | OH-827372E | Support Structure |  | ED-16358 | Secondary Distribution Line | Unknown |  | No |  | No |  | Yes | 2023-11-20 02:00 | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Local FD | No |  |  | Non-HFTD | 34.1232 | -117.3217 | 98115 | 83954674 | ED-16358 | SCE | ES-8021 | SHIRAZ | Other, see comment | A | Overhead | 12 | -99 | Pepper | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.9949 | 965543711
43 | 6 | FIPA_2023_1108_1109 | SCE | ES-8039 | SCE-3216 | 129797000 |  | 2023-11-08 19:09 | 2023 | Utility staff |  | Equipment failure | [6 empty] | Other, see comment | Underground Cable | 12 | 12 |  | Subsurface | Utility personnel |  |  |  | UG-5055195 | Support Structure |  | ED-05318 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Fire-resistive fuel bed |  | <3 meters of linear travel | Unknown |  | No |  |  | Non-HFTD | 34.0828 | -117.2953 | 99013 | 83954676 | ED-16358 | SCE | ES-8021 | SHIRAZ | Other, see comment | A | Overhead | 12 | -99 | Pepper | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 16360.5705 | 965543783
44 | 20 | FIPA_2023_1214_1416 | SCE | ES-5672 | SCE-2889 |  |  | 2023-12-14 22:16 | 2023 | Fire agency |  | Vandalism/theft | [8 empty] | 12 | 12 |  | Overhead | Utility personnel |  |  |  | OH-X5249E | Support Structure |  | ED-06833 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Structure |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | San Bernardino County Fire | No |  |  | Non-HFTD | 34.1394 | -117.3793 | 117388 | 113773281 | ED-06833 | SCE | ES-5672 | FRISBIE | Other, see comment | A | Overhead | 12 | -99 | Alder | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.1168 | 965621613
45 | 14 | FIPA_2023_1208_1102 | SCE | ES-5899 | SCE-3048 | 129936499 |  | 2023-12-08 19:02 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Eucalyptus | sp. | Eucalyptus |  |  | 12 | 12 |  | Overhead | Utility personnel |  | Conductor: Secondary |  | OH-4400521E | Support Structure |  | ED-18280 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Orange County Fire Authority | No |  |  | Non-HFTD | 33.7662 | -117.9938 | 163456 | 197196738 | ED-18280 | SCE | ES-5899 | TULSA | Other, see comment | A | Overhead | 12 | -99 | Trask | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2569 | 965784773
46 | 2 | FIPA_2023_1029_1839 | SCE | ES-5555 | SCE-2045 | 129753216 |  | 2023-10-30 01:39 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 16 | 16 |  | Overhead | Utility personnel |  |  |  | OH-3004910E | Support Structure |  | ED-05930 | Secondary Distribution Line | Weather |  | Yes | 2023-10-29 10:00 | No |  | Yes | 2023-10-29 06:00 | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 34.2566 | -118.6419 | 350111 | 303557608 | ED-05930 | SCE | ES-5555 | ENERGY | Other, see comment | A | Overhead | 16 | -99 | Chatsworth | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2021-02-22 | 2021 | 0-9 | -99 |  | Unknown | 0.00347982 | 0.00347938 | 4.41845E-0 | 3.1292 | 965163903
47 | 11 | FIPA_2023_1014_0034 | SCE | ES-5577 | SCE-2865 | 129663584 |  | 2023-10-14 07:34 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 16 | 16 |  | Overhead | Utility personnel |  |  |  | OH-1024615E | Support Structure |  | ED-13885 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Fire agency | Ventura County Fire Department | No |  |  | Non-HFTD | 34.2433 | -119.2154 | 350111 | 303557608 | ED-05930 | SCE | ES-5555 | ENERGY | Other, see comment | A | Overhead | 16 | -99 | Chatsworth | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2021-02-22 | 2021 | 0-9 | -99 |  | Unknown | 0.00347982 | 0.00347938 | 4.41845E-0 | 173237.7213 | 965163903
48 | 3 | FIPA_2023_1004_1708 | SCE | ES-5330 | SCE-2133 | 129610723 |  | 2023-10-05 00:08 | 2023 | Utility staff |  | Vegetation contact |  |  |  | Eucalyptus | sp. | Eucalyptus |  |  | 12 | 12 |  | Overhead | Utility personnel |  | Conductor: Primary |  | OH-4622260E | Support Structure |  | ED-19150 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Self-extinguished |  | No |  |  | Non-HFTD | 36.3593 | -119.1526 | 387182 | 67664461 | ED-19150 | SCE | ES-5330 | WELLS | Other, see comment | A | Overhead | 12 | -99 | Venida | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.0014 | 965561513
49 | 18 | FIPA_2023_1210_1216 | SCE | ES-5257 | SCE-2977 | 129946372 |  | 2023-12-10 20:16 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 4 | 4 |  | Overhead | Utility personnel |  |  |  | OH-1791416E | Support Structure |  | ED-06172 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Structure |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Los Angeles County Fire | No |  |  | Non-HFTD | 33.8967 | -118.3296 | 509132 | 218666702 | ED-06172 | SCE | ES-5257 | EZRA | Other, see comment | A | Overhead | 4 | -99 | Bridge | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.788 | 965846994
50 | 13 | FIPA_2023_1023_0531 | SCE | ES-5711 | SCE-2424 | 129725408 |  | 2023-10-23 12:31 | 2023 | Fire agency |  | Vandalism/theft | [8 empty] | 16 | 16 |  | Overhead | Utility personnel |  |  |  | OH-4074928e | Support Structure |  | ED-19822 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Other, see comment | Vehicle | Fire-resistive fuel bed |  | <3 meters of linear travel | Fire agency | Los Angeles Fire Department | No |  |  | Non-HFTD | 33.8695 | -118.2092 | 606301 | 218319622 | ED-19822 | SCE | ES-5711 | ZENO | Other, see comment | A | Overhead | 16 | -99 | Carson | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 2.9856 | 965751296
51 | 15 | FIPA_2023_1026_1644 | SCE | ES-5636 | SCE-2932 | 129739482 |  | 2023-10-26 23:44 | 2023 | Other, see comment | Calimesa Police Department | Equipment failure | [6 empty] | Other, see comment | Pothead | 12 | 12 |  | Overhead | Utility personnel |  |  |  | OH-4331309E | Support Structure |  | ED-03934 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire | No |  |  | Tier 3 | 33.9807 | -117.0503 | 666327 | 84004196 | ED-03934 | SCE | ES-5636 | CONINE | Covered |  | Overhead | 12 | -99 | Yucaipa | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown | 0.00072287 | 0.00072287 | 0 | 3.3691 | 965525038
52 | 17 | FIPA_2023_1029_1349 | SCE | ES-5035 | SCE-2133 |  |  | 2023-10-29 20:49 | 2023 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 220 | 220 |  | Overhead | Utility personnel |  | Insulator |  | M121T | Support Structure |  | NA | Transmission Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Kern County Fire Department | No |  |  | Non-HFTD | 35.6025 | -119.0875 | 720149 | 67648997 | ED-03170 | SCE | ES-5328 | CATTLE | Other, see comment | A | Overhead | 12 | -99 | Tulare | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 232879.9933 | 965213080
53 | 10 | FIPA_2023_1120_0745 | SCE | ES-5835 | SCE-3048 | 129848959 |  | 2023-11-20 15:45 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Cupressus | Cupressus sempervirens | Italian Cypress |  |  | 12 | 12 |  | Overhead | Utility personnel |  | Conductor: Primary |  | OH-1568821E | Support Structure |  | ED-11618 | Primary Distribution Line | Weather |  | No |  | No |  | Yes | 2023-11-20 02:00 | Urban | Vegetation |  | Fire-resistive fuel bed |  | <3 meters of linear travel | Fire agency | Orange County Fire Authority | No |  |  | Non-HFTD | 33.7503 | -117.8289 | 804690 | 197168450 | ED-11618 | SCE | ES-5835 | MELISSA | Other, see comment | A | Overhead | 12 | -99 | La Veta | Aluminum conductor steel reinforced (ACSR) |  | 4 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 3.2761 | 965445110
54 | 5 | FIPA_2023_1006_2334 | SCE | ES-5838 | SCE-3471 | 129625516 |  | 2023-10-07 06:34 | 2023 | Other, see comment | Los Angeles County Sheriff | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 |  | Overhead | Utility personnel |  | Support structure |  | OH-4506227E | Support Structure |  | ED-09390 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Los Angeles County Fire | No |  |  | Non-HFTD | 34.0051 | -118.0683 | 899331 | 340418560 | ED-18000 | SCE | ES-5838 | TORPEDO | Other, see comment | A | Overhead | 12 | -99 | Narrows | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 7.0534 | 965757401
55 | 4 | FIPA_2023_1030_0358 | SCE | ES-5060 | SCE-2103 | 129754250 |  | 2023-10-30 10:58 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Quercus | Quercus wislizeni A. DC | Interior Live Oak |  |  | 12 | 12 |  | Overhead | Utility personnel |  | Support structure |  | OH-454329E | Support Structure |  | ED-06357 | Primary Distribution Line | Weather |  | No |  | No |  | Yes | 2023-10-29 06:00 | Rural | Vegetation |  | Timber fuel model |  | 0.26-9.99 | Fire agency | Angeles Fire | No |  | Environ Hold prevented SCE from removing tree before event | Tier 3 | 34.2191 | -117.6617 | 951309 | 325970473 | ED-06357 | SCE | ES-5060 | FERRARA | Other, see comment | A | Overhead | 12 | -99 | Padua | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 2019-06-05 | 2019 | 0-9 | -99 |  | Unknown | 3.62237E-0 | 2.68662E-0 | 9.35746E-0 | 3.1166 | 965818894
56 | 1 | FIPA_2023_1002_1536 | SCE | ES-5328 | SCE-2133 |  |  | 2023-10-02 22:36 | 2023 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 |  | Overhead | Utility personnel |  | Jumper |  | OH-885169E | Support Structure |  | ED-02845 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Fire agency | Tulare County Fire Department | No |  |  | Non-HFTD | 36.2132 | -119.328 | 997479 | 67649257 | ED-02845 | SCE | ES-5328 | CANBY | Other, see comment | A | Overhead | 12 | -99 | Tulare | Aluminum conductor steel reinforced (ACSR) |  | 336 | [5 empty] | Unknown | -99 |  | Unknown |  |  |  | 7.1369 | 965204681
57 | 7 | FIPA_2023_1009_2057 | SCE | ES-8018 | SCE-3001 | 129637889 |  | 2023-10-10 03:57 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 |  | Overhead | Utility personnel |  |  |  | OH-4402000E | Support Structure |  | ED-16349 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire | No |  |  | Tier 2 | 33.5847 | -117.1179 | 1066101 | 120302905 | ED-16492 | SCE | ES-8018 | SKINNER | Other, see comment | A | Overhead | 33 | -99 | Auld | Aluminum conductor steel reinforced (ACSR) |  | 653 | [5 empty] | Unknown | -99 |  | Unknown | 0.00378117 | 0.00378117 | 0 | 9.3243 | 965709374
58 | 16 | FIPA_2023_1210_1113 | SCE | ES-5594 | SCE-2944 | 129945500 |  | 2023-12-10 19:16 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Transformer |  | 16 | 16 |  | Overhead | Utility personnel |  |  |  | OH-1712771E | Support Structure |  | ED-12616 | Primary Distribution Line | Unknown |  | Yes | 2023-12-09 16:00 | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Los Angeles County Fire | No |  |  | Tier 3 | 34.4347 | -118.531 | 1145155 | 10487088 | ED-12616 | SCE | ES-5594 | NERO | Other, see comment | UNKNOWN | Overhead | 16 | -99 | Haskell | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown | 1.77522E-0 | 1.70343E-0 | 7.17925E-0 | 3.0216 | 965153597
59 | 19 | FIPA_2023_1029_1810 | SCE | ES-8132 | SCE-2355 | 129752757 |  | 2023-10-30 01:10 | 2023 | Public |  | Vandalism/theft | [8 empty] | 12 | 12 |  | Subsurface | Utility personnel |  |  |  | UG-5000049 | Support Structure |  | ED-02255 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Unknown |  | No |  |  | Non-HFTD | 35.1323 | -117.9311 | 1145155 | 10487088 | ED-12616 | SCE | ES-5594 | NERO | Other, see comment | UNKNOWN | Overhead | 16 | -99 | Haskell | Other, see comment | UNKNOWN | UNKNOWN | [5 empty] | Unknown | -99 |  | Unknown | 1.77522E-0 | 1.70343E-0 | 7.17925E-0 | 311238.8196 | 965153597
60 | 8 | FIPA_2023_1115_0740 | SCE | ES-5114 | SCE-2972 |  |  | 2023-11-15 15:40 | 2023 | Fire agency |  | Vegetation contact |  |  |  | Bambusa | Phyllostachys aurea | Bamboo |  |  | 4 | 4 |  | Overhead | Utility personnel |  | Conductor: Secondary |  | OH-1614974E | Support Structure |  | ED-02270 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Los Angeles Fire Department | No |  |  | Non-HFTD | 34.0435 | -118.1878 | 1171647 | 329543998 | ED-17690 | SCE | ES-5101 | TEST | Other, see comment | A | Overhead | 16 | -99 | Alhambra | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-08-27 | 2019 | 0-9 | -99 |  | Unknown |  |  |  | 22803.318 | 917171962
61 | 9 | FIPA_2023_1011_1400 | SCE | ES-5101 | SCE-2972 | 129649112 |  | 2023-10-11 21:00 | 2023 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 16 | 16 |  | Overhead | Utility personnel |  |  |  | OH-203013E | Support Structure |  | ED-17690 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Urban | Other, see comment | Patio/Deck | Fire-resistive fuel bed |  | <0.25 | Fire agency | Pasadena Fire Department | No |  |  | Non-HFTD | 34.101 | -118.1579 | 1171647 | 329543998 | ED-17690 | SCE | ES-5101 | TEST | Other, see comment | A | Overhead | 16 | -99 | Alhambra | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-08-27 | 2019 | 0-9 | -99 |  | Unknown |  |  |  | 2.9898 | 917171962

## SCE_Ignition_Lines_22
OBJECTID_12 | OBJECTID | IgnitionID | UtilityID | SubstationID | NearestWeatherStationID | ToutageID | DoutageID | FireStartDateTime | FireStartYear | FireDetectionMethod | FireDetectionMethodComment | SuspectedInitiatingCause | SuspectedInitiatingCauseComment | ObjectContact | ObjectContactComment | VegetationGenus | VegetationSpecies | VegetationCommonName | EquipmentFailure | EquipmentFailureComment | AssociatedNominalVoltagekV | AssociatedOperatingVoltagekV | OtherCompanies | EquipmentType | Determination | DeterminationComment | FacilityContacted | FacilityContactedComment | ContributingFactor | ContributingFactorComment | RFWStatus | RFWIssueDateTime | FWWStatus | FWWIssueDateTime | HWWStatus | HWWIssueDateTime | OriginLandUse | MaterialAtOrigin | MaterialAtOriginComment | FuelBedDescription | FuelBedDescriptionComment | FireSize | SuppressedBy | SuppressingAgency | FireInvestigation | FireAHJ | OutageStatus | IgnitionNotes | Confidential | HFTDClass | County | District | Latitude | Longitude | OBJECTID_1 | CircuitID | UtilityID_1 | SubstationID_1 | LineClass | CircuitName | County_1 | ConductorType | ConductorTypeComment | AssetOHUG | NominalVoltagekV | OperatingVoltagekV | SubstationName | ConductorMaterial | ConductorMaterialComment | ConductorSize | ConductorOD | LastInspectionDate | LastMaintenanceDate | InstallationDate | InstallationYear | EstimatedAge | UsefulLifespan | AmpacityRating | Greased | Confidential_1 | Distance
1 | 12 | FIPA_2022_0211_1319 | SCE | ES-5239 | SCE-2218 |  | 126504858 | 2022-02-11 13:19 | 2022 | Utility staff |  | Object contact |  | Vehicle contact - car pole |  |  |  |  | N/A |  | 16 |  | T-Mobile, Verizon Wireless, AT&T Mobility, Corwn C | Overhead | Utility personnel |  | Support structure (pole or tower) |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  |  |  | No |  | No | Tier 3 | Los Angeles | Thousand Oaks | 34.1069 | -118.7149 | 6306 | 2173091 | SCE | 2743 | Primary Distribution | Mulholland | Los Angeles | Bare |  | Overhead | 16 | -99 | Crater | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 22.3313
2 | 11 | FIPA_2022_0207_0859 | SCE | ES-5306 | SCE-2570 |  | 126483157 | 2022-02-07 08:59 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Splice |  | 12 |  | N/A | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Unknown |  |  |  | Yes |  | No | Non-HFTD | Tulare | Tulare | 35.8923 | -119.2508 | 153494 | 2187042 | SCE | 2825 | Primary Distribution | Tarusa | Tulare | Other - see comment | Unknown | Overhead | 12 | -99 | Venice Hill | Other - see comment | Unknown | 2/0 |  |  |  |  | -99 | Unknown |  | 405 | Unknown | No | 72218.4595
3 | 8 | FIPA_2022_0204_1615 | SCE | ES-5329 | SCE-2133 |  | 126470085 | 2022-02-04 16:15 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Transformer |  | 12 |  | N/A | Overhead | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Tulare County FD |  |  | Yes |  | No | Non-HFTD | Tulare | Tulare | 36.4142 | -119.1889 | 201182 | 2188194 | SCE | 2825 | Primary Distribution | Twin Butte | Tulare | Bare |  | Overhead | 12 | -99 | Venice Hill | ACSR |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 10.6322
4 | 7 | FIPA_2022_0204_1051 | SCE | ES-5056 | SCE-2254 |  | 126471274 | 2022-02-04 10:51 | 2022 | Public |  | Object contact |  | Vegetation contact |  | Eucalyptus | SPP | Eucalyptus | N/A |  | 16 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Ventura County FD |  |  | Yes |  | No | Tier 3 | Ventura | Thousand Oaks | 34.2806 | -118.9031 | 658914 | 2190554 | SCE | 2743 | Primary Distribution | Rhoda | Los Angeles | Bare |  | Overhead | 16 | -99 | Crater | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 31343.312
5 | 9 | FIPA_2022_0215_2040 | SCE | ES-5503 | SCE-2173 |  | 126524600 | 2022-02-15 20:40 | 2022 | Utility staff |  | Object contact |  | Vegetation contact |  | Quercus | SPP | Oak | N/A |  | 16 |  | N/A | Overhead | Utility personnel |  | Conductor - Primary |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Brush, dirt, and asphalt | <0.25 | Fire agency | Carpinteria FD |  |  | Yes |  | No | Non-HFTD | Santa Barbara | Santa Barbara | 34.4093 | -119.5151 | 658914 | 2190554 | SCE | 2743 | Primary Distribution | Rhoda | Los Angeles | Bare |  | Overhead | 16 | -99 | Crater | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 97909.5032
6 | 15 | FIPA_2022_0129_1000 | SCE | ES-5056 | SCE-3035 |  | N/A | 2022-01-29 10:00 | 2022 | Fire agency |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 16 |  | N/A | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Other - see comment | Building | Other - see comment | Side of house | <0.25 | Fire agency | Ventura County FD |  |  | No |  | No | Tier 3 | Ventura | Thousand Oaks | 34.2632 | -118.8953 | 658914 | 2190554 | SCE | 2743 | Primary Distribution | Rhoda | Los Angeles | Bare |  | Overhead | 16 | -99 | Crater | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 29035.9849
7 | 16 | FIPA_2022_0311_1100 | SCE | ES-5012 | SCE-2972 |  | 126637480 | 2022-03-11 11:00 | 2022 | Utility staff |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 16 |  | N/A | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Local FD - not listed on ED46 |  |  | Yes |  | No | Non-HFTD | Los Angeles | Montebello | 34.0348 | -118.1118 | 978387 | 2165214 | SCE | 2687 | Primary Distribution | Davie | Los Angeles | Bare |  | Overhead | 16 | -99 | Vail | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  |  | Unknown | No | 4160.8279
8 | 1 | FIPA_2022_0106_1214 | SCE | ES-5164 | SCE-2972 |  | 126314731 | 2022-01-06 12:14 | 2022 | Utility staff |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 16 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Structure |  | Fire-resistive fuel bed |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | Los Angeles | Montebello | 34.0477 | -118.1622 | 1107201 | 2141575 | SCE | 2687 | Primary Distribution | Flotilla | Los Angeles | Bare |  | Overhead | 16 | -99 | Vail | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  |  | Unknown | No | 6686.4665
9 | 13 | FIPA_2022_0212_1326 | SCE | ES-5175 | SCE-2360 |  | 126508807 | 2022-02-12 13:26 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 16 |  | AT&T California | Overhead | Utility personnel |  |  |  | External Force |  | No |  | No |  | No |  | Urban | Other - see comment | Trash and debris | Fire-resistive fuel bed |  | <0.25 | Unknown |  |  |  | No |  | No | Non-HFTD | Los Angeles | Dominguez Hills | 34.0069 | -118.1278 | 1107201 | 2141575 | SCE | 2687 | Primary Distribution | Flotilla | Los Angeles | Bare |  | Overhead | 16 | -99 | Vail | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  |  | Unknown | No | 10.1589
10 | 2 | FIPA_2022_0109_1610 | SCE | ES-5144 | SCE-2635 |  | 126329805 | 2022-01-09 16:10 | 2022 | Utility staff |  | Object contact |  | Animal contact |  |  |  |  | N/A |  | 4 |  | Frontier Communications | Overhead | Utility personnel |  | Service drop |  | External Force |  | No |  | No |  | No |  | Urban | Structure |  | Brush fuel model |  | <0.25 | Fire agency | Duarte FD |  |  | No |  | No | Non-HFTD | Los Angeles | Monrovia | 34.1582 | -118.0546 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 8218.6654
11 | 3 | FIPA_2022_0121_2130 | SCE | ES-5171 | SCE-3037 |  | N/A | 2022-01-21 21:30 | 2022 | Other - see comment | Customer | Wire-to-wire contact |  | N/A |  |  |  |  | N/A |  | 16 |  | Frontier Communications | Overhead | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Urban | Other - see comment | Wooden fence | Grass fuel model |  | <0.25 | Unknown |  |  |  | No |  | No | Non-HFTD | Los Angeles | Monrovia | 34.1337 | -117.987 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 36.673
12 | 4 | FIPA_2022_0123_0926 | SCE | ES-8049 | SCE-2802 |  | 126408269 | 2022-01-23 09:26 | 2022 | Utility staff |  | Object contact |  | Vehicle contact - car pole |  |  |  |  | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Support structure (pole or tower) |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Victorville FD |  |  | Yes |  | No | Non-HFTD | San Bernardino | Victorville | 34.506 | -117.3878 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 83458.6662
13 | 5 | FIPA_2022_0112_0110 | SCE | ES-8004 | SCE-2704 |  | 126341497 | 2022-01-12 01:10 | 2022 | Fire agency |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 12 |  | Frontier Communications | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Fire agency | Palm Springs FD |  |  | Yes |  | No | Non-HFTD | Riverside | Palm Springs | 33.8137 | -116.5319 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 167523.3204
14 | 6 | FIPA_2022_0125_1512 | SCE | ES-5158 | SCE-3045 |  | 126418206 | 2022-01-25 15:12 | 2022 | Utility staff |  | Object contact |  | Vegetation contact |  | Quercus | SPP | Oak | N/A |  | 16 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Other - see comment | Wood shed | Other - see comment | Concrete slab, grass, and dirt | <0.25 | Unknown |  |  |  | Yes |  | No | Tier 2 | Los Angeles | Monrovia | 34.1999 | -118.1706 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 22305.2162
15 | 10 | FIPA_2022_0127_1358 | SCE | ES-5171 | SCE-2608 |  | 126431522 | 2022-01-27 13:58 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 16 |  | Frontier Communications | Overhead | Utility personnel |  |  |  | External Force |  | No |  | No |  | No |  | Urban | Other - see comment | Vehicle | Fire-resistive fuel bed |  | <0.25 | Fire agency | Monrovia FD |  |  | No |  | No | Non-HFTD | Los Angeles | Monrovia | 34.1337 | -117.987 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 36.673
16 | 14 | FIPA_2022_0223_0529 | SCE | ES-8275 | SCE-2332 |  | 126560770 | 2022-02-23 05:29 | 2022 | Utility staff |  | Object contact |  | Vegetation contact |  | Platanus | occidentalis | Sycamore | N/A |  | 12 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | Riverside | Ontario | 33.8579 | -117.5881 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 57759.3476
17 | 17 | FIPA_2022_0311_1527 | SCE | ES-8089 | SCE-3067 |  | 126638738 | 2022-03-11 15:27 | 2022 | Utility staff |  | Object contact |  | Other - see comment | Trash truck snagged overhead c |  |  |  | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Service drop |  | External Force |  | No |  | No |  | No |  | Urban | Other - see comment | Debris inside of garbage truck | Other - see comment | Corrugate debris in a garbage truck | <0.25 | Fire agency | Riverside Country FD |  |  | Yes |  | No | Non-HFTD | Riverside | Menifee | 33.7364 | -116.92 | 1169286 | 2167763 | SCE | 2684 | Primary Distribution | Hurstview | Los Angeles | Bare |  | Overhead | 16 | -99 | Bradbury | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 130139.1904
18 | 8 | FIPA_2022_0422_0704 | SCE | ES-8044 | SCE-2188 |  | 126827715 | 2022-04-22 07:04 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 33 |  | N/A | Overhead | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Tier 2 | RIVERSIDE | PALM SPRINGS | 34.0292 | -116.6075 | 60854 | 2140670 | SCE | 3264 | Primary Distribution | Coachella | RIVERSIDE | Bare |  | Overhead | 33 | -99 | Garnet | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 0.91634
19 | 2 | FIPA_2022_0408_1641 | SCE | ES-5510 | SCE-2112 |  |  | 2022-04-08 16:41 | 2022 | Utility staff |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 16 |  | N/A | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Non-HFTD | VENTURA | VENTURA | 34.3982 | -118.9139 | 79343 | 2133017 | SCE | 2889 | Primary Distribution | Barrington | VENTURA | Bare |  | Overhead | 16 | -99 | Fillmore | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 0.99705
20 | 7 | FIPA_2022_0416_1457 | SCE | ES-8504 | SCE-2573 |  |  | 2022-04-16 14:57 | 2022 | Utility staff |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 12 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | LACFD | No |  | Yes |  | No | Tier 3 | LOS ANGELES | ANTELOPE VALLEY | 34.5901 | -118.2032 | 85500 | 2160626 | SCE | 3428 | Primary Distribution | Huckleberry | LOS ANGELES | Bare |  | Overhead | 12 | -99 | Ritter Ranch | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 1.1651
21 | 6 | FIPA_2022_0414_1242 | SCE | ES-5033 | SCE-2192 | 14783 |  | 2022-04-14 12:42 | 2022 | Utility staff |  | Object contact |  | Animal contact |  |  |  |  | N/A |  | 66 |  | N/A | Overhead | Utility personnel |  | Conductor - Transmission |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Tulare County Fire Department | No |  | No |  | No | Tier 2 | TULARE | TULARE | 36.0947 | -118.9706 | 176271 | 2184717 | SCE | 2825 | Primary Distribution | St. Johns | TULARE | Bare |  | Overhead | 12 | -99 | Venice Hill | Other - see comment | C | 6 |  |  |  |  | -99 | Unknown |  | 140 | Unknown | No | 48980.07
22 | 15 | FIPA_2022_0511_1200 | SCE | ES-5329 | SCE-2133 |  |  | 2022-05-11 12:00 | 2022 | Utility staff |  | Object contact |  | Vegetation contact |  | Unknown - not in SCE inventory | Unknown - not in SCE inventory | Unknown - not in SCE inventory | N/A |  | 12 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Rural | Structure |  | Timber fuel model |  | <0.25 | Fire agency | Tulare City FD | No |  | Yes |  | No | Non-HFTD | TULARE | TULARE | 36.3889 | -119.2174 | 176271 | 2184717 | SCE | 2825 | Primary Distribution | St. Johns | TULARE | Bare |  | Overhead | 12 | -99 | Venice Hill | Other - see comment | C | 6 |  |  |  |  | -99 | Unknown |  | 140 | Unknown | No | 1.3101
23 | 1 | FIPA_2022_0402_0411 | SCE | ES-5518 | SCE-2361 |  | 126731358 | 2022-04-02 04:11 | 2022 | Utility staff |  | Object contact |  | Vehicle contact - car pole |  |  |  |  | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Support structure (pole or tower) |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Other - see comment | Cardboard debris | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | LOS ANGELES | VICTORVILLE | 34.4986 | -117.7454 | 259396 |  | SCE |  | Primary Distribution |  | LOS ANGELES | Bare |  | Overhead | -99 | -99 |  | Other - see comment | C | 4 |  |  |  |  | -99 | Unknown |  | 190 | Unknown | No | 1.2022
24 | 12 | FIPA_2022_0506_2022 | SCE | ES-8044 | SCE-2691 |  |  | 2022-05-06 20:22 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Other |  | 33 |  | N/A | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | RIVERSIDE | PALM SPRINGS | 33.8576 | -116.5463 | 294536 | 2190593 | SCE | 3264 | Primary Distribution | Tram | RIVERSIDE | Bare |  | Overhead | 33 | -99 | Garnet | Other - see comment | C | 2 |  |  |  |  | -99 | Unknown |  | 260 | Unknown | No | 1.2579
25 | 13 | FIPA_2022_0507_1524 | SCE | ES-7026 | SCE-2641 |  | 126906229 | 2022-05-07 15:24 | 2022 | Fire agency |  | Object contact |  | Animal contact |  |  |  |  | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Transformer |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino County FD | No |  | No |  | No | Non-HFTD | SAN BERNARDINO | VICTORVILLE | 34.799 | -117.281 | 315732 | 2135465 | SCE | 2121073 | Primary Distribution | Armijo | SAN BERNARDINO | Bare |  | Overhead | 12 | -99 | Armijo P.T. | Other - see comment | C | 6 |  |  |  |  | -99 | Unknown |  | 140 | Unknown | No | 1.4174
26 | 4 | FIPA_2022_0413_1448 | SCE | ES-5055 | SCE-2053 |  | 126787295 | 2022-04-13 14:48 | 2022 | Utility staff |  | Object contact |  | Vehicle contact - car pole |  |  |  |  | N/A |  | 16 |  | N/A | Overhead | Utility personnel |  | Support structure (pole or tower) |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Santa Barbara County FD | No |  | Yes |  | No | Tier 3 | SANTA BARBARA | SANTA BARBARA | 34.4414 | -119.9234 | 553145 | 2133433 | SCE | 2592 | Primary Distribution | Bidder | SANTA BARBARA | Bare |  | Overhead | 16 | -99 | Goleta | Other - see comment | C | 2/0 |  |  |  |  | -99 | Unknown |  | 405 | Unknown | No | 1.0374
27 | 5 | FIPA_2022_0413_1830 | SCE | ES-5055 | SCE-2053 |  | 126787295 | 2022-04-13 18:30 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Switch |  | 16 |  | N/A | Overhead | Utility personnel |  |  |  | Other - see comment | Horizontal Omni Rupter Switch | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Self-extinguished |  | No |  | Yes |  | No | Tier 3 | SANTA BARBARA | SANTA BARBARA | 34.4634 | -119.9227 | 578337 | 2133433 | SCE | 2592 | Primary Distribution | Bidder | SANTA BARBARA | Bare |  | Overhead | 16 | -99 | Goleta | Other - see comment | C | 2/0 |  |  |  |  | -99 | Unknown |  | 405 | Unknown | No | 1.2461
28 | 17 | FIPA_2022_0517_1140 | SCE | ES-8013 | SCE-2641 |  | 126950598 | 2022-05-17 11:40 | 2022 | Fire agency |  | Object contact |  | Vegetation contact |  | Tamarix | SPP | Athel | N/A |  | 12 |  | Frontier Communications | Overhead | Utility personnel |  | Service drop |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Apple Valley Fire Department | No |  | No |  | No | Non-HFTD | SAN BERNARDINO | VICTORVILLE | 34.4823 | -117.205 | 613332 | 2148115 | SCE | 3236 | Primary Distribution | Deloro | SAN BERNARDINO | Bare |  | Overhead | 12 | -99 | Apple Valley | ACSR |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.082
29 | 14 | FIPA_2022_0508_1456 | SCE | ES-5101 | SCE-2300 |  |  | 2022-05-08 14:56 | 2022 | Utility staff |  | Object contact |  | Animal contact |  |  |  |  | N/A |  | 16 |  | AT&T California, Crown Castle | Overhead | Utility personnel |  | Recloser |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | South Pasadena FD | No |  | Yes |  | No | Tier 2 | LOS ANGELES | MONROVIA | 34.1119 | -118.1714 | 627305 | 2190348 | SCE | 2627 | Primary Distribution | Test | LOS ANGELES | Covered |  | Overhead | 16 | -99 | Alhambra | ACSR |  | 336 |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 1.0819
30 | 9 | FIPA_2022_0423_1000 | SCE | ES-5874 | SCE-2992 |  | 126834576 | 2022-04-23 10:00 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Transformer |  | 12 |  | N/A | Subsurface | Utility personnel |  |  |  | Other - see comment | Internal failure on BURD trans | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Orange County FD | No |  | Yes |  | No | Non-HFTD | ORANGE | SADDLEBACK | 33.6362 | -117.8174 | 630138 | 19230547 | SCE | 3197 | Primary Distribution | Jaguar | ORANGE | Bare |  | Overhead | 12 | -99 | Lampson | ACSR |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 22873.115
31 | 10 | FIPA_2022_0424_1134 | SCE | ES-8808 | SCE-3048 |  | 126837546 | 2022-04-24 11:34 | 2022 | Utility staff |  | Object contact |  | Balloon contact |  |  |  |  | N/A |  | 12 |  | Frontier Communicaitons | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Tree top | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | ORANGE | HUNTINGTON BEACH | 33.739 | -118.0199 | 736655 | 2162584 | SCE | 3446 | Primary Distribution | Jazz | ORANGE | Bare |  | Overhead | 12 | -99 | Team | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 1.0067
32 | 11 | FIPA_2022_0505_1031 | SCE | ES-5679 | SCE-3060 |  | 126897605 | 2022-05-05 10:31 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 12 |  | AT&T California | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | RIVERSIDE | ONTARIO | 33.842 | -117.5512 | 751715 | 2164822 | SCE | 3037 | Primary Distribution | Griffin | RIVERSIDE | Bare |  | Overhead | 12 | -99 | Chase | ACSR |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 0.97601
33 | 19 | FIPA_2022_0528_1053 | SCE | ES-5049 | SCE-2261 | 14838 |  | 2022-05-28 10:53 | 2022 | Utility staff |  | Contamination |  | N/A |  |  |  |  | N/A |  | 66 |  | N/A | Overhead | Utility personnel |  |  |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Ventura County FD | No |  | No |  | No | Tier 3 | VENTURA | THOUSAND OAKS | 34.2031 | -118.8207 | 796825 | 2133017 | SCE | 2889 | Primary Distribution | Barrington | VENTURA | Bare |  | Overhead | 16 | -99 | Fillmore | ACSR |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 28269.5156
34 | 18 | FIPA_2022_0525_1320 | SCE | ES-5049 | SCE-2900 |  |  | 2022-05-25 13:20 | 2022 | Utility staff |  | Contamination |  | N/A |  |  |  |  | N/A |  | 66 |  | N/A | Overhead | Utility personnel |  |  |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Oxnard FD | No |  | No |  | No | Non-HFTD | VENTURA | VENTURA | 34.1512 | -119.1183 | 1068718 | 2189111 | SCE | 2937 | Primary Distribution | Sidewinder | VENTURA | Other - see comment | Unknown | Overhead | 16 | -99 | Estero | Other - see comment | Unknown | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 2.3146
35 | 3 | FIPA_2022_0408_1939 | SCE | ES-5870 | SCE-3048 |  |  | 2022-04-08 19:39 | 2022 | Utility staff |  | Object contact |  | Animal contact |  |  |  |  | N/A |  | 12 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Structure |  | Other - see comment | Building | <0.25 | Fire agency | Orange County FD | No |  | Yes |  | No | Non-HFTD | ORANGE | SANTA ANA | 33.7861 | -117.9179 | 1088635 | 19230547 | SCE | 3197 | Primary Distribution | Jaguar | ORANGE | Bare |  | Overhead | 12 | -99 | Lampson | ACSR |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 0.98516
36 | 16 | FIPA_2022_0514_1144 | SCE | ES-8030 | SCE-2592 |  | 126936343 | 2022-05-14 11:44 | 2022 | Utility staff |  | Equipment failure |  | N/A |  |  |  |  | Conductor |  | 33 |  | N/A | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | SAN BERNARDINO | BARSTOW | 35.5045 | -115.4344 | 1100898 | 2187295 | SCE | 3252 | Primary Distribution | Nipton | SAN BERNARDINO | Bare |  | Overhead | 33 | -99 | Mountain Pass | ACSR |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.0945
37 | 8 | FIPA_2022_0729_1803 | SCE | ES-5526 | SCE-2148 | N/A | 127319918 | 2022-07-29 18:03 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 16 |  | None | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Tier 3 | VENTURA | VENTURA | 34.454 | -119.2322 | 39927 | 2178918 | SCE | 2895 | Primary Distribution | Pancho | VENTURA | Bare |  | Overhead | 16 | -99 | Camarillo | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 40621.1973
38 | 10 | FIPA_2022_0809_1907 | SCE | ES-5517 | SCE-2208 | N/A | 127372472 | 2022-08-09 19:07 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 16 |  | None | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Ventura County FD | No |  | Yes |  | No | Non-HFTD | VENTURA | VENTURA | 34.2177 | -119.0058 | 39927 | 2178918 | SCE | 2895 | Primary Distribution | Pancho | VENTURA | Bare |  | Overhead | 16 | -99 | Camarillo | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 2.4439
39 | 14 | FIPA_2022_0824_1533 | SCE | N/A | SCE-2680 | N/A | N/A | 2022-08-24 15:33 | 2022 | Utility staff | N/A | Object contact | N/A | Animal contact |  | N/A | N/A | N/A | N/A | N/A | 66 |  | None | Overhead | Utility personnel |  | Other - see comment | Circuit Breaker | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Customer |  | No |  | No |  | No | Tier 3 | VENTURA | VENTURA | 34.313 | -119.1857 | 39927 | 2178918 | SCE | 2895 | Primary Distribution | Pancho | VENTURA | Bare |  | Overhead | 16 | -99 | Camarillo | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 23787.6886
40 | 15 | FIPA_2022_0901_1400 | SCE | ES-5519 | SCE-2406 | N/A | 127502084 | 2022-09-01 14:00 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 16 |  | AT&T California | Overhead | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Local FD | No |  | Yes |  | No | Tier 3 | LOS ANGELES | THOUSAND OAKS | 34.1595 | -118.7324 | 106754 | 2144093 | SCE | 2897 | Primary Distribution | Crumner | LOS ANGELES | Other - see comment | UNKNOWN | Overhead | 16 | -99 | Malibu | Other - see comment | UNKNOWN | UNKNOWN |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 1.2253
41 | 3 | FIPA_2022_0710_1953 | SCE | ES-5056 | SCE-2255 | N/A | N/A | 2022-07-10 19:53 | 2022 | Utility staff | N/A | Object contact | N/A | Animal contact |  | N/A | N/A | N/A | N/A | N/A | 16 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Tier 3 | VENTURA | THOUSAND OAKS | 34.2443 | -118.8293 | 113288 | 2134918 | SCE | 2593 | Primary Distribution | Brennan | VENTURA | Other - see comment | UNKNOWN | Overhead | 16 | -99 | Moorpark | Other - see comment | UNKNOWN | UNKNOWN |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 1.1426
42 | 16 | FIPA_2022_0904_1300 | SCE | ES-5569 | SCE-2261 | N/A | 127522185 | 2022-09-04 13:00 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Transformer | N/A | 16 |  | None | Subsurface | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Ventura County FD | No |  | No |  | No | Tier 3 | VENTURA | THOUSAND OAKS | 34.214 | -118.8433 | 113288 | 2134918 | SCE | 2593 | Primary Distribution | Brennan | VENTURA | Other - see comment | UNKNOWN | Overhead | 16 | -99 | Moorpark | Other - see comment | UNKNOWN | UNKNOWN |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 4370.5727
43 | 2 | FIPA_2022_0708_2245 | SCE | N/A | SCE-2063 | N/A | N/A | 2022-07-08 22:45 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 220 |  | None | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | LACFD | No |  | No |  | No | Tier 3 | LOS ANGELES | VALENCIA | 34.4746 | -118.608 | 118008 | 2186869 | SCE | 2909 | Primary Distribution | Stearns | VENTURA | Bare |  | Overhead | 16 | -99 | Santa Susana | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 28141.7992
44 | 18 | FIPA_2022_0908_1632 | SCE | N/A | SCE-2396 | N/A | N/A | 2022-09-08 16:32 | 2022 | Utility staff | N/A | Object contact | N/A | Animal contact |  | N/A | N/A | N/A | N/A | N/A | 220 |  | None | Overhead | Utility personnel |  | Insulator |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Kern County FD | No |  | No |  | No | Non-HFTD | KERN |  | 35.6215 | -119.0393 | 118073 | 2186869 | SCE | 2909 | Primary Distribution | Stearns | VENTURA | Bare |  | Overhead | 16 | -99 | Santa Susana | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 185173.9294
45 | 20 | FIPA_2022_0929_1446 | SCE | N/A | SCE-2396 | N/A | N/A | 2022-09-29 14:46 | 2022 | Utility staff | N/A | Object contact | N/A | Animal contact |  | N/A | N/A | N/A | N/A | N/A | 220 |  | None | Overhead | Utility personnel |  | Conductor - Transmission |  | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Non-HFTD | KERN |  | 35.6027 | -119.0361 | 118073 | 2186869 | SCE | 2909 | Primary Distribution | Stearns | VENTURA | Bare |  | Overhead | 16 | -99 | Santa Susana | Aluminum conductor steel reinforced (ACSR) |  | 653 |  |  |  |  | -99 | Unknown |  | 920 | Unknown | No | 182575.2752
46 | 9 | FIPA_2022_0807_1200 | SCE | ES-5532 | SCE-2144 | N/A | N/A | 2022-08-07 12:00 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 16 |  | AT&T California | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Junk pile | <0.25 | Unknown |  | No |  | No |  | No | Tier 3 | VENTURA | THOUSAND OAKS | 34.2845 | -118.713 | 118130 | 2186869 | SCE | 2909 | Primary Distribution | Stearns | VENTURA | Bare |  | Overhead | 16 | -99 | Santa Susana | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 1.192
47 | 13 | FIPA_2022_0819_1850 | SCE | ES-5550 | N/A | N/A | N/A | 2022-08-19 18:50 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 16 |  | None | Overhead | Utility personnel |  |  |  | Other - see comment | Potential grow house caused ov | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Tier 3 | LOS ANGELES | VALENCIA | 34.287 | -118.3739 | 211476 |  | SCE |  | Primary Distribution |  | LOS ANGELES | Covered |  | Overhead | -99 | -99 |  | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 0.49608
48 | 1 | FIPA_2022_0704_1835 | SCE | ES-5832 | SCE-2955 | N/A | 127194161 | 2022-07-04 18:35 | 2022 | Utility staff | N/A | Object contact | N/A | Balloon contact |  | N/A | N/A | N/A | N/A | N/A | 12 |  | AT&T California | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Brea FD, Fullerton FD | No |  | Yes |  | No | Non-HFTD | ORANGE | FULLERTON | 33.9036 | -117.9141 | 336345 | 15508626 | SCE | 3166 | Primary Distribution | Grace | ORANGE | Bare |  | Overhead | 12 | -99 | La Habra | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.1749
49 | 5 | FIPA_2022_0713_0707 | SCE | ES-5086 | SCE-3048 | N/A | 127229997 | 2022-07-13 07:07 | 2022 | Utility staff | N/A | Object contact | N/A | Animal contact |  | N/A | N/A | N/A | N/A | N/A | 12 |  | None | Pad-mounted | Utility personnel |  | Transformer |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Plants | <0.25 | Unknown |  | No |  | No |  | No | Non-HFTD | ORANGE | HUNTINGTON BEACH | 33.6858 | -117.9549 | 336345 | 15508626 | SCE | 3166 | Primary Distribution | Grace | ORANGE | Bare |  | Overhead | 12 | -99 | La Habra | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 29460.8649
50 | 17 | FIPA_2022_0905_1650 | SCE | ES-8810 | SCE-2633 | N/A | 127535002 | 2022-09-05 16:50 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Connector device | N/A | 12 |  | None | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Tier 2 | ORANGE | SADDLEBACK | 33.6229 | -117.6177 | 336345 | 15508626 | SCE | 3166 | Primary Distribution | Grace | ORANGE | Bare |  | Overhead | 12 | -99 | La Habra | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 49960.8158
51 | 4 | FIPA_2022_0710_1122 | SCE | ES-5518 | SCE-2181 | N/A | N/A | 2022-07-10 11:22 | 2022 | Utility staff | N/A | Object contact | N/A | Balloon contact |  | N/A | N/A | N/A | N/A | N/A | 12 |  | None | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | LOS ANGELES | ANTELOPE VALLEY | 34.5715 | -117.9341 | 526267 | 2190583 | SCE | 2896 | Primary Distribution | Titan | LOS ANGELES | Covered |  | Overhead | 12 | -99 | Little Rock | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 1.0102
52 | 19 | FIPA_2022_0909_1746 | SCE | ES-7123 | SCE-2555 | N/A | 127573663 | 2022-09-09 17:46 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Fuse | N/A | 2.4 |  | None | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Customer |  | No |  | Yes |  | No | Tier 2 | TULARE | TULARE | 35.8709 | -118.6384 | 526267 | 2190583 | SCE | 2896 | Primary Distribution | Titan | LOS ANGELES | Covered |  | Overhead | 12 | -99 | Little Rock | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 193421.436
53 | 6 | FIPA_2022_0717_1830 | SCE | ES-8214 | SCE-2699 | N/A | 127253820 | 2022-07-17 18:30 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Connector device | N/A | 4.16 |  | None | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | Palm Springs Fire Department | No |  | Yes |  | No | Tier 2 | RIVERSIDE | PALM SPRINGS | 33.8014 | -116.5468 | 649276 | 2181201 | SCE | 3294 | Primary Distribution | Player | RIVERSIDE | Bare |  | Overhead | 33 | -99 | Eisenhower | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 0.98932
54 | 7 | FIPA_2022_0718_1702 | SCE | ES-5069 | SCE-3050 | N/A | 127260501 | 2022-07-18 17:02 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 12 |  | None | Pad-mounted | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Structure |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | No |  | No | Non-HFTD | SAN BERNARDINO | ONTARIO | 34.0052 | -117.5887 | 654222 | 2189337 | SCE | 3260 | Primary Distribution | Urbita | SAN BERNARDINO | Bare |  | Overhead | 12 | -99 | Homart | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 30571.9406
55 | 11 | FIPA_2022_0811_0409 | SCE | ES-8039 | SCE-2988 | N/A | 127380160 | 2022-08-11 04:09 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Capacitor bank | N/A | 12 |  | AT&T California | Overhead | Utility personnel |  |  |  | Other - see comment | Equipment defect | No |  | No |  | No |  | Rural | Structure |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino County FD | No |  | No |  | No | Non-HFTD | SAN BERNARDINO | REDLANDS | 34.0267 | -117.3147 | 654222 | 2189337 | SCE | 3260 | Primary Distribution | Urbita | SAN BERNARDINO | Bare |  | Overhead | 12 | -99 | Homart | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 1.0512
56 | 12 | FIPA_2022_0814_0353 | SCE | ES-8021 | SCE-2960 | N/A | 127400417 | 2022-08-14 03:53 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  | N/A | N/A | N/A | Conductor | N/A | 12 |  | None | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  | No |  | Yes |  | No | Non-HFTD | SAN BERNARDINO | FOOTHILL | 34.0879 | -117.3886 | 654222 | 2189337 | SCE | 3260 | Primary Distribution | Urbita | SAN BERNARDINO | Bare |  | Overhead | 12 | -99 | Homart | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 11584.5663
57 | 1 | FIPA_2022_1002_1527 | SCE | ES-5055 | SCE-2183 |  | 127714318 | 2022-10-02 15:27 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  |  |  |  | Conductor |  | 16 |  | N/A | Overhead | Utility personnel |  |  |  | Human Error |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Santa Barbara County FD | No |  | Yes |  | No | Tier 3 | SANTA BARBARA | SANTA BARBARA | 34.4479 | -119.8574 | 1496 | 2188027 | SCE | 2592 | Primary Distribution | Trump | SANTA BARBARA | Bare |  | Overhead | 16 | -99 | Goleta | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.0859
58 | 4 | FIPA_2022_1024_2107 | SCE | ES-5504 | SCE-2203 |  | N/A | 2022-10-24 21:07 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  |  |  |  | Splice/Clamp/Connector |  | 16 |  | N/A | Overhead | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Unknown |  |  |  | No |  | No | Tier 3 | VENTURA | VENTURA | 34.3339 | -119.385 | 15407 | 2180276 | SCE | 2883 | Primary Distribution | Red Mountain | VENTURA | Bare |  | Overhead | 16 | -99 | Casitas | Other - see comment | C | 2/0 |  |  |  |  | -99 | Unknown |  | 405 | Unknown | No | 0.76012
59 | 6 | FIPA_2022_1102_0107 | SCE | ES-5505 | SCE-2227 |  | N/A | 2022-11-02 01:07 | 2022 | Fire agency | N/A | Equipment failure | N/A | N/A |  |  |  |  | Transformer |  | 16 |  | N/A | Overhead | Utility personnel |  |  |  | Weather |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Small palms and dirt | <0.25 | Fire agency | Ventura City FD | No |  | No |  | No | Non-HFTD | VENTURA | VENTURA | 34.2184 | -119.0652 | 35670 | 2181729 | SCE | 2884 | Primary Distribution | Mugu | VENTURA | Bare |  | Overhead | 16 | -99 | Colonia | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 1.8676
60 | 8 | FIPA_2022_1116_1000 | SCE | ES-5236 | SCE-2069 |  | 127988290 | 2022-11-16 10:00 | 2022 | Fire agency | N/A | Object contact | N/A | Vegetation contact |  | Eucalyptus | sp. | Eucalyptus | N/A |  | 16 |  | Frontier Communications | Overhead | Utility personnel |  | Guy/span wire |  | Weather |  | Yes | 2022-11-16 08:00 | Yes | 2022-11-16 08:00 | Yes | 2022-11-15 19:00 | Rural | Vegetation |  | Grass fuel model |  | <0.25 | Fire agency | LACFD | No |  | Yes |  | No | Tier 3 | LOS ANGELES | THOUSAND OAKS | 34.0966 | -118.5992 | 110704 | 2190638 | SCE | 2741 | Primary Distribution | Vicasa | LOS ANGELES | Covered |  | Overhead | 16 | -99 | Valdez | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 0 | Unknown | No | 1.5723
61 | 9 | FIPA_2022_1121_2230 | SCE | ES-5074 | SCE-2360 |  | 128021432 | 2022-11-21 22:30 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  |  |  |  | Conductor |  | 16 |  | Verizon Wireless & AT&T California | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | LOS ANGELES | DOMINGUEZ HILLS | 33.983 | -118.1269 | 190586 | 2139637 | SCE | 2608 | Primary Distribution | Cal Strip | LOS ANGELES | Bare |  | Overhead | 16 | -99 | Laguna Bell | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 1.0912
62 | 7 | FIPA_2022_1104_1237 | SCE | ES-5856 | SCE-3048 |  | 127887115 | 2022-11-04 12:37 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  |  |  |  | Transformer |  | 12 |  | N/A | Pad-mounted | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Urban | Structure |  | Brush fuel model |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | ORANGE | SANTA ANA | 33.7746 | -117.8803 | 277338 | 2190323 | SCE | 3185 | Primary Distribution | Penalty | ORANGE | Bare |  | Overhead | 12 | -99 | Washington | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 21.8191
63 | 3 | FIPA_2022_1010_2243 | SCE | ES-8076 | SCE-2840 |  | 127760724 | 2022-10-10 22:43 | 2022 | Utility staff | N/A | Equipment failure | N/A | N/A |  |  |  |  | Transformer |  | 12 |  | N/A | Pad-mounted | Utility personnel |  |  |  | Other - see comment | Grid shows overloading over co | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Utility |  |  |  | Yes |  | No | Tier 2 | SAN BERNARDINO | REDLANDS | 34.0748 | -117.2685 | 304076 | 2161012 | SCE | 3383 | Primary Distribution | Interpace | RIVERSIDE | Bare |  | Overhead | 33 | -99 | Corona | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 32868.9049
64 | 10 | FIPA_2022_1123_2229 | SCE | ES-8159 | SCE-2274 |  | 128028617 | 2022-11-23 22:29 | 2022 | Fire agency | N/A | Object contact | N/A | Vegetation contact |  | N/A | N/A | Tumble Weed | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Conductor - Primary |  | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Fire-resistive fuel bed |  | 0.26-9.99 | Fire agency | CAL Fire | No |  | Yes |  | No | Tier 2 | RIVERSIDE | ONTARIO | 33.858 | -117.4333 | 304076 | 2161012 | SCE | 3383 | Primary Distribution | Interpace | RIVERSIDE | Bare |  | Overhead | 33 | -99 | Corona | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  |  | -99 | Unknown |  | 605 | Unknown | No | 0.97076
65 | 11 | FIPA_2022_1127_0839 | SCE | ES-5186 | SCE-2914 |  | 128039504 | 2022-11-27 08:39 | 2022 | Fire agency | N/A | Object contact | N/A | Vegetation contact |  |  |  | Palm Frond | N/A |  | 12 |  | Frontier Communications | Overhead | Utility personnel |  | Conductor - Primary |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Other - see comment | Unable to determine with visual provided | <0.25 | Fire agency | Local FD | No |  | Yes |  | No | Non-HFTD | LOS ANGELES | COVINA | 34.0976 | -117.8246 | 403807 | 2168702 | SCE | 2696 | Primary Distribution | Egmont | LOS ANGELES | Bare |  | Overhead | 12 | -99 | Cortez | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  |  | -99 | Unknown |  | 280 | Unknown | No | 0.70092
66 | 2 | FIPA_2022_1009_1738 | SCE | ES-5539 | SCE-2828 |  | 127751133 | 2022-10-09 17:38 | 2022 | Utility staff | N/A | Object contact | N/A | Vehicle contact - car pole |  |  |  |  | N/A |  | 12 |  | N/A | Overhead | Utility personnel |  | Guy/span wire |  | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | LOS ANGELES | ANTELOPE VALLEY | 34.5809 | -118.1203 | 494322 | 2190984 | SCE | 2915 | Primary Distribution | Quinby | LOS ANGELES | Bare |  | Overhead | 12 | -99 | Anaverde | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.34
67 | 12 | FIPA_2022_1129_0332 | SCE | ES-8137 | SCE-2279 |  | N/A | 2022-11-29 03:32 | 2022 | Fire agency | N/A | Vandalism/theft | N/A | N/A |  |  |  |  | Conductor |  | 12 |  | Frontier Communications | Subsurface | Utility personnel |  |  |  | External Force |  | No |  | No |  | No |  | Rural | Structure |  | Grass fuel model |  | <0.25 | Fire agency | Kern County FD | No |  | No |  | No | Non-HFTD | KERN | RIDGECREST | 35.6 | -117.7032 | 494322 | 2190984 | SCE | 2915 | Primary Distribution | Quinby | LOS ANGELES | Bare |  | Overhead | 12 | -99 | Anaverde | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 146161.0077
68 | 5 | FIPA_2022_1030_0338 | SCE | ES-8139 | SCE-2592 |  | 127857800 | 2022-10-30 03:38 | 2022 | Utility staff | N/A | Unknown | N/A | N/A |  |  |  |  | Secondary Riser |  | 12 |  | Frontier Communications | Subsurface | Utility personnel |  |  |  | Unknown |  | No |  | No |  | No |  | Rural | Structure |  | Brush fuel model |  | <0.25 | Unknown |  |  |  | Yes |  | No | Non-HFTD | RIVERSIDE | BLYTHE | 33.605 | -114.7206 | 753385 | 2174772 | SCE | 3316 | Primary Distribution | Leak | RIVERSIDE | Bare |  | Overhead | 12 | -99 | Dunes | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  |  | -99 | Unknown |  | 160 | Unknown | No | 1.1601

## IgnitionSummary
IgnitionID | NearestWeatherStationID | DoutageID | FireStartDateTime | SuspectedInitiatingCause | ObjectContact | EquipmentFailure | HFTDClass | FireSize | CircuitName | ConductorType
FIPA_2022_0211_1319 | SCE-2218 | 126504858 | 2022-02-11 13:19 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | <0.25 | Mulholland | Bare
FIPA_2022_0207_0859 | SCE-2570 | 126483157 | 2022-02-07 08:59 | Equipment failure | N/A | Splice | Non-HFTD | <3 meters of linear travel | Tarusa | Other - see comment
FIPA_2022_0204_1615 | SCE-2133 | 126470085 | 2022-02-04 16:15 | Equipment failure | N/A | Transformer | Non-HFTD | <0.25 | Twin Butte | Bare
FIPA_2022_0204_1051 | SCE-2254 | 126471274 | 2022-02-04 10:51 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Rhoda | Bare
FIPA_2022_0215_2040 | SCE-2173 | 126524600 | 2022-02-15 20:40 | Object contact | Vegetation contact | N/A | Non-HFTD | <0.25 | Rhoda | Bare
FIPA_2022_0129_1000 | SCE-3035 | N/A | 2022-01-29 10:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Rhoda | Bare
FIPA_2022_0311_1100 | SCE-2972 | 126637480 | 2022-03-11 11:00 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Davie | Bare
FIPA_2022_0106_1214 | SCE-2972 | 126314731 | 2022-01-06 12:14 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Flotilla | Bare
FIPA_2022_0212_1326 | SCE-2360 | 126508807 | 2022-02-12 13:26 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Flotilla | Bare
FIPA_2022_0109_1610 | SCE-2635 | 126329805 | 2022-01-09 16:10 | Object contact | Animal contact | N/A | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0121_2130 | SCE-3037 | N/A | 2022-01-21 21:30 | Wire-to-wire contact | N/A | N/A | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0123_0926 | SCE-2802 | 126408269 | 2022-01-23 09:26 | Object contact | Vehicle contact - car pole | N/A | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0112_0110 | SCE-2704 | 126341497 | 2022-01-12 01:10 | Object contact | Balloon contact | N/A | Non-HFTD | <3 meters of linear travel | Hurstview | Bare
FIPA_2022_0125_1512 | SCE-3045 | 126418206 | 2022-01-25 15:12 | Object contact | Vegetation contact | N/A | Tier 2 | <0.25 | Hurstview | Bare
FIPA_2022_0127_1358 | SCE-2608 | 126431522 | 2022-01-27 13:58 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0223_0529 | SCE-2332 | 126560770 | 2022-02-23 05:29 | Object contact | Vegetation contact | N/A | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0311_1527 | SCE-3067 | 126638738 | 2022-03-11 15:27 | Object contact | Other - see comment | N/A | Non-HFTD | <0.25 | Hurstview | Bare
FIPA_2022_0422_0704 | SCE-2188 | 126827715 | 2022-04-22 07:04 | Equipment failure | N/A | Conductor | Tier 2 | <0.25 | Coachella | Bare
FIPA_2022_0408_1641 | SCE-2112 |  | 2022-04-08 16:41 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Barrington | Bare
FIPA_2022_0416_1457 | SCE-2573 |  | 2022-04-16 14:57 | Object contact | Balloon contact | N/A | Tier 3 | <0.25 | Huckleberry | Bare
FIPA_2022_0414_1242 | SCE-2192 |  | 2022-04-14 12:42 | Object contact | Animal contact | N/A | Tier 2 | 0.26-9.99 | St. Johns | Bare
FIPA_2022_0511_1200 | SCE-2133 |  | 2022-05-11 12:00 | Object contact | Vegetation contact | N/A | Non-HFTD | <0.25 | St. Johns | Bare
FIPA_2022_0402_0411 | SCE-2361 | 126731358 | 2022-04-02 04:11 | Object contact | Vehicle contact - car pole | N/A | Non-HFTD | <0.25 |  | Bare
FIPA_2022_0506_2022 | SCE-2691 |  | 2022-05-06 20:22 | Equipment failure | N/A | Other | Non-HFTD | <0.25 | Tram | Bare
FIPA_2022_0507_1524 | SCE-2641 | 126906229 | 2022-05-07 15:24 | Object contact | Animal contact | N/A | Non-HFTD | <0.25 | Armijo | Bare
FIPA_2022_0413_1448 | SCE-2053 | 126787295 | 2022-04-13 14:48 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | 0.26-9.99 | Bidder | Bare
FIPA_2022_0413_1830 | SCE-2053 | 126787295 | 2022-04-13 18:30 | Equipment failure | N/A | Switch | Tier 3 | <0.25 | Bidder | Bare
FIPA_2022_0517_1140 | SCE-2641 | 126950598 | 2022-05-17 11:40 | Object contact | Vegetation contact | N/A | Non-HFTD | <0.25 | Deloro | Bare
FIPA_2022_0508_1456 | SCE-2300 |  | 2022-05-08 14:56 | Object contact | Animal contact | N/A | Tier 2 | <0.25 | Test | Covered
FIPA_2022_0423_1000 | SCE-2992 | 126834576 | 2022-04-23 10:00 | Equipment failure | N/A | Transformer | Non-HFTD | <0.25 | Jaguar | Bare
FIPA_2022_0424_1134 | SCE-3048 | 126837546 | 2022-04-24 11:34 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Jazz | Bare
FIPA_2022_0505_1031 | SCE-3060 | 126897605 | 2022-05-05 10:31 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Griffin | Bare
FIPA_2022_0528_1053 | SCE-2261 |  | 2022-05-28 10:53 | Contamination | N/A | N/A | Tier 3 | 0.26-9.99 | Barrington | Bare
FIPA_2022_0525_1320 | SCE-2900 |  | 2022-05-25 13:20 | Contamination | N/A | N/A | Non-HFTD | <0.25 | Sidewinder | Other - see comment
FIPA_2022_0408_1939 | SCE-3048 |  | 2022-04-08 19:39 | Object contact | Animal contact | N/A | Non-HFTD | <0.25 | Jaguar | Bare
FIPA_2022_0514_1144 | SCE-2592 | 126936343 | 2022-05-14 11:44 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Nipton | Bare
FIPA_2022_0729_1803 | SCE-2148 | 127319918 | 2022-07-29 18:03 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Pancho | Bare
FIPA_2022_0809_1907 | SCE-2208 | 127372472 | 2022-08-09 19:07 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Pancho | Bare
FIPA_2022_0824_1533 | SCE-2680 | N/A | 2022-08-24 15:33 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Pancho | Bare
FIPA_2022_0901_1400 | SCE-2406 | 127502084 | 2022-09-01 14:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Crumner | Other - see comment
FIPA_2022_0710_1953 | SCE-2255 | N/A | 2022-07-10 19:53 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Brennan | Other - see comment
FIPA_2022_0904_1300 | SCE-2261 | 127522185 | 2022-09-04 13:00 | Equipment failure | N/A | Transformer | Tier 3 | <0.25 | Brennan | Other - see comment
FIPA_2022_0708_2245 | SCE-2063 | N/A | 2022-07-08 22:45 | Equipment failure | N/A | Conductor | Tier 3 | 0.26-9.99 | Stearns | Bare
FIPA_2022_0908_1632 | SCE-2396 | N/A | 2022-09-08 16:32 | Object contact | Animal contact | N/A | Non-HFTD | 0.26-9.99 | Stearns | Bare
FIPA_2022_0929_1446 | SCE-2396 | N/A | 2022-09-29 14:46 | Object contact | Animal contact | N/A | Non-HFTD | <0.25 | Stearns | Bare
FIPA_2022_0807_1200 | SCE-2144 | N/A | 2022-08-07 12:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Stearns | Bare
FIPA_2022_0819_1850 | N/A | N/A | 2022-08-19 18:50 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 |  | Covered
FIPA_2022_0704_1835 | SCE-2955 | 127194161 | 2022-07-04 18:35 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Grace | Bare
FIPA_2022_0713_0707 | SCE-3048 | 127229997 | 2022-07-13 07:07 | Object contact | Animal contact | N/A | Non-HFTD | <0.25 | Grace | Bare
FIPA_2022_0905_1650 | SCE-2633 | 127535002 | 2022-09-05 16:50 | Equipment failure | N/A | Connector device | Tier 2 | <0.25 | Grace | Bare
FIPA_2022_0710_1122 | SCE-2181 | N/A | 2022-07-10 11:22 | Object contact | Balloon contact | N/A | Non-HFTD | <0.25 | Titan | Covered
FIPA_2022_0909_1746 | SCE-2555 | 127573663 | 2022-09-09 17:46 | Equipment failure | N/A | Fuse | Tier 2 | <0.25 | Titan | Covered
FIPA_2022_0717_1830 | SCE-2699 | 127253820 | 2022-07-17 18:30 | Equipment failure | N/A | Connector device | Tier 2 | <0.25 | Player | Bare
FIPA_2022_0718_1702 | SCE-3050 | 127260501 | 2022-07-18 17:02 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Urbita | Bare
FIPA_2022_0811_0409 | SCE-2988 | 127380160 | 2022-08-11 04:09 | Equipment failure | N/A | Capacitor bank | Non-HFTD | <0.25 | Urbita | Bare
FIPA_2022_0814_0353 | SCE-2960 | 127400417 | 2022-08-14 03:53 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Urbita | Bare
FIPA_2022_1002_1527 | SCE-2183 | 127714318 | 2022-10-02 15:27 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Trump | Bare
FIPA_2022_1024_2107 | SCE-2203 | N/A | 2022-10-24 21:07 | Equipment failure | N/A | Splice/Clamp/Connector | Tier 3 | 0.26-9.99 | Red Mountain | Bare
FIPA_2022_1102_0107 | SCE-2227 | N/A | 2022-11-02 01:07 | Equipment failure | N/A | Transformer | Non-HFTD | <0.25 | Mugu | Bare
FIPA_2022_1116_1000 | SCE-2069 | 127988290 | 2022-11-16 10:00 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Vicasa | Covered
FIPA_2022_1121_2230 | SCE-2360 | 128021432 | 2022-11-21 22:30 | Equipment failure | N/A | Conductor | Non-HFTD | <0.25 | Cal Strip | Bare
FIPA_2022_1104_1237 | SCE-3048 | 127887115 | 2022-11-04 12:37 | Equipment failure | N/A | Transformer | Non-HFTD | <0.25 | Penalty | Bare
FIPA_2022_1010_2243 | SCE-2840 | 127760724 | 2022-10-10 22:43 | Equipment failure | N/A | Transformer | Tier 2 | <0.25 | Interpace | Bare
FIPA_2022_1123_2229 | SCE-2274 | 128028617 | 2022-11-23 22:29 | Object contact | Vegetation contact | N/A | Tier 2 | 0.26-9.99 | Interpace | Bare
FIPA_2022_1127_0839 | SCE-2914 | 128039504 | 2022-11-27 08:39 | Object contact | Vegetation contact | N/A | Non-HFTD | <0.25 | Egmont | Bare
FIPA_2022_1009_1738 | SCE-2828 | 127751133 | 2022-10-09 17:38 | Object contact | Vehicle contact - car pole | N/A | Non-HFTD | <0.25 | Quinby | Bare
FIPA_2022_1129_0332 | SCE-2279 | N/A | 2022-11-29 03:32 | Vandalism/theft | N/A | Conductor | Non-HFTD | <0.25 | Quinby | Bare
FIPA_2022_1030_0338 | SCE-2592 | 127857800 | 2022-10-30 03:38 | Unknown | N/A | Secondary Riser | Non-HFTD | <0.25 | Leak | Bare
FIPA_2023_0214_2129 | SCE-3048 | 128407122 | 2023-02-14 | Equipment failure |  | Connector device | Non-HFTD | <3 meters of linear travel | PARROT | Other, see comment
FIPA_2023_0114_2218 | SCE-2976 | 128261538 | 2023-01-14 | Vegetation contact |  |  | Non-HFTD | <0.25 | PAPOOSE | Other, see comment
FIPA_2023_0224_0641 | SCE-2133 | 128463887 | 2023-02-24 | Equipment failure |  | Insulator and bushing | Non-HFTD | <3 meters of linear travel | TAYLOR | Bare
FIPA_2023_0226_1605 | SCE-2592 | 128504283 | 2023-02-26 | Equipment failure |  | Insulator and bushing | Non-HFTD | <0.25 | EIGHTEENTH | Other, see comment
FIPA_2023_0609_2119 | SCE-2809 | 129018104 | 2023-06-10 04:19 | Equipment failure |  | Connector device | Tier 3 | <0.25 | CANET | Other, see comment
FIPA_2023_0513_1639 | SCE-2796 | 128890731 | 2023-05-13 23:39 | Equipment failure |  | Lightning arrester | Non-HFTD | <0.25 | PUEBLO | Other, see comment
FIPA_2023_0522_1538 | SCE-2972 |  | 2023-05-22 22:38 | Object contact | Balloon contact |  | Non-HFTD | <0.25 | HELM | Other, see comment
FIPA_2023_0428_1216 | SCE-2884 | 128828523 | 2023-04-28 19:16 | Object contact | Balloon contact |  | Non-HFTD | <0.25 | ZUNI | Other, see comment
FIPA_2023_0512_1830 | SCE-2473 | 128887878 | 2023-05-13 01:30 | Equipment failure |  | Connector device | Non-HFTD | <3 meters of linear travel | BOXCAR | Other, see comment
FIPA_2023_0513_0918 | SCE-2831 | 128889128 | 2023-05-13 16:18 | Object contact | Land vehicle contact |  | Non-HFTD | <3 meters of linear travel |  | Other, see comment
FIPA_2023_0508_0833 | SCE-2641 |  | 2023-05-08 15:33 | Object contact | Animal contact |  | Non-HFTD | <0.25 | BURNETTA | Other, see comment
FIPA_2023_0606_1128 | SCE-2279 | 129000346 | 2023-06-06 18:28 | Object contact | Land vehicle contact |  | Non-HFTD | <0.25 | DEETER | Other, see comment
FIPA_2023_0607_1659 | SCE-2279 | 129005011 | 2023-06-07 23:59 | Object contact | Animal contact |  | Non-HFTD | <0.25 | HIGHWAY SIX | Other, see comment
FIPA_2023_0616_1127 | SCE-2133 | 129045355 | 2023-06-16 18:27 | Equipment failure |  | Lightning arrester | Non-HFTD | <0.25 | CATTLE | Other, see comment
FIPA_2023_0508_0248 | SCE-2846 |  | 2023-05-08 09:48 | Vandalism/theft |  |  | Non-HFTD | <0.25 | GAMBLE | Other, see comment
FIPA_2023_0425_0849 | SCE-3011 |  | 2023-04-25 15:49 | Vandalism/theft |  |  | Non-HFTD | <3 meters of linear travel | GAMBLE | Other, see comment
FIPA_2023_0507_1358 | SCE-2641 | 128865914 | 2023-05-07 20:58 | Object contact | Animal contact |  | Non-HFTD | <0.25 | SENECA | Other, see comment
FIPA_2023_0403_1658 | SCE-2641 | 128716701 | 2023-04-03 23:58 | Equipment failure |  | Insulator and bushing | Non-HFTD | <3 meters of linear travel | KNOLLS | Other, see comment
FIPA_2023_0707_1344 | SCE-2934 | 129142217 | 2023-07-07 20:44 | Object contact | Animal contact |  | Non-HFTD | 0.26-9.99 | DEACON | Other, see comment
FIPA_2023_0726_0252 | SCE-2641 |  | 2023-07-26 09:52 | Equipment failure |  | Connector device | Non-HFTD | <3 meters of linear travel | VERDEMONT | Other, see comment
FIPA_2023_0804_1139 | SCE-2267 |  | 2023-08-04 18:39 | Equipment failure |  | Conductor | Tier 2 | <3 meters of linear travel | VERDEMONT | Other, see comment
FIPA_2023_0723_0951 | SCE-3081 | 129217433 | 2023-07-23 16:51 | Object contact | Balloon contact |  | Non-HFTD | 0.26-9.99 | NAPA | Other, see comment
FIPA_2023_0808_0521 | SCE-2869 | 129310056 | 2023-08-08 12:21 | Contamination |  |  | Non-HFTD | <3 meters of linear travel | PEDRO | Bare
FIPA_2023_0708_0000 | SCE-3002 |  | 2023-07-08 07:00 | Object contact | Balloon contact |  | Non-HFTD | <3 meters of linear travel | DAMERAL | Other, see comment
FIPA_2023_0703_1935 | SCE-2691 | 129129206 | 2023-07-04 02:35 | Equipment failure |  | Conductor | Non-HFTD | <3 meters of linear travel | FEY | Other, see comment
FIPA_2023_0705_0856 | SCE-2573 | 129132941 | 2023-07-05 15:56 | Object contact | Animal contact |  | Non-HFTD | 0.26-9.99 | ENDOR | Other, see comment
FIPA_2023_0808_1253 | SCE-3047 |  | 2023-08-08 19:53 | Object contact | Animal contact |  | Non-HFTD | <3 meters of linear travel | NORWOOD | Other, see comment
FIPA_2023_0715_1148 | SCE-2216 |  | 2023-07-15 18:48 | Equipment failure |  | Conductor | Tier 3 | <3 meters of linear travel | CLARINET | Other, see comment
FIPA_2023_0716_0103 | SCE-2216 | 129184852 | 2023-07-16 08:03 | Wire-to-wire contact |  |  | Tier 3 | <0.25 | CLARINET | Other, see comment
FIPA_2023_0720_1227 | SCE-2934 |  | 2023-07-20 19:27 | Object contact | Land vehicle contact |  | Non-HFTD | 0.26-9.99 | WARDELL | Other, see comment
FIPA_2023_0703_2112 | SCE-3010 | 129127716 | 2023-07-04 04:12 | Equipment failure |  | Connector device | Tier 2 | <3 meters of linear travel | WARDELL | Other, see comment
FIPA_2023_0807_1051 | SCE-2246 |  | 2023-08-07 17:51 | Object contact | Land vehicle contact |  | Non-HFTD | <3 meters of linear travel | WHIP | Other, see comment
FIPA_2023_0706_1200 | SCE-2767 |  | 2023-07-06 19:00 | Equipment failure |  | Conductor | Non-HFTD | <3 meters of linear travel | BISSELL | Other, see comment
FIPA_2023_0713_2046 | SCE-2952 | 129169822 | 2023-07-14 03:46 | Equipment failure |  | Other, see comment | Non-HFTD | <0.25 | BONVIEW | Other, see comment
FIPA_2023_0815_1656 | SCE-2307 | 129328592 | 2023-08-15 23:56 | Equipment failure |  | Insulator and bushing | Tier 3 | <0.25 | GALAHAD | Covered
FIPA_2023_0703_0951 | SCE-3075 | 129125822 | 2023-07-03 16:51 | Equipment failure |  | Conductor | Non-HFTD | <3 meters of linear travel | DAMERAL | Other, see comment
FIPA_2023_0725_1239 | SCE-3068 | 129227678 | 2023-07-25 19:39 | Vandalism/theft |  |  | Non-HFTD | <0.25 | FONRI | Other, see comment
FIPA_2023_0712_1208 | SCE-2187 |  | 2023-07-12 19:08 | Object contact | Animal contact |  | Tier 3 | 0.26-9.99 | SALVADOR | Other, see comment
FIPA_2023_0705_0124 | SCE-2424 |  | 2023-07-05 08:24 | Equipment failure |  | Conductor | Non-HFTD | <3 meters of linear travel | RANSOM | Other, see comment
FIPA_2023_0710_0710 | SCE-3048 | 129151420 | 2023-07-10 14:10 | Equipment failure |  | Conductor | Non-HFTD | <3 meters of linear travel | DORIS | Other, see comment
FIPA_2023_0902_1715 | SCE-2972 | 129454855 | 2023-09-03 00:15 | Equipment failure |  | Conductor | Non-HFTD | <0.25 | LOMAS | Other, see comment
FIPA_2023_1120_2014 | SCE-2996 | 129856470 | 2023-11-21 04:14 | Vegetation contact |  |  | Non-HFTD | <0.25 | SHIRAZ | Other, see comment
FIPA_2023_1108_1109 | SCE-3216 | 129797000 | 2023-11-08 19:09 | Equipment failure |  | Other, see comment | Non-HFTD | <3 meters of linear travel | SHIRAZ | Other, see comment
FIPA_2023_1214_1416 | SCE-2889 |  | 2023-12-14 22:16 | Vandalism/theft |  |  | Non-HFTD | <0.25 | FRISBIE | Other, see comment
FIPA_2023_1208_1102 | SCE-3048 | 129936499 | 2023-12-08 19:02 | Vegetation contact |  |  | Non-HFTD | <0.25 | TULSA | Other, see comment
FIPA_2023_1029_1839 | SCE-2045 | 129753216 | 2023-10-30 01:39 | Equipment failure |  | Conductor | Tier 3 | <0.25 | ENERGY | Other, see comment
FIPA_2023_1014_0034 | SCE-2865 | 129663584 | 2023-10-14 07:34 | Equipment failure |  | Connector device | Non-HFTD | <3 meters of linear travel | ENERGY | Other, see comment
FIPA_2023_1004_1708 | SCE-2133 | 129610723 | 2023-10-05 00:08 | Vegetation contact |  |  | Non-HFTD | 0.26-9.99 | WELLS | Other, see comment
FIPA_2023_1210_1216 | SCE-2977 | 129946372 | 2023-12-10 20:16 | Equipment failure |  | Conductor | Non-HFTD | <0.25 | EZRA | Other, see comment
FIPA_2023_1023_0531 | SCE-2424 | 129725408 | 2023-10-23 12:31 | Vandalism/theft |  |  | Non-HFTD | <3 meters of linear travel | ZENO | Other, see comment
FIPA_2023_1026_1644 | SCE-2932 | 129739482 | 2023-10-26 23:44 | Equipment failure |  | Other, see comment | Tier 3 | 0.26-9.99 | CONINE | Covered
FIPA_2023_1029_1349 | SCE-2133 |  | 2023-10-29 20:49 | Object contact | Animal contact |  | Non-HFTD | 0.26-9.99 | CATTLE | Other, see comment
FIPA_2023_1120_0745 | SCE-3048 | 129848959 | 2023-11-20 15:45 | Vegetation contact |  |  | Non-HFTD | <3 meters of linear travel | MELISSA | Other, see comment
FIPA_2023_1006_2334 | SCE-3471 | 129625516 | 2023-10-07 06:34 | Object contact | Land vehicle contact |  | Non-HFTD | <0.25 | TORPEDO | Other, see comment
FIPA_2023_1030_0358 | SCE-2103 | 129754250 | 2023-10-30 10:58 | Vegetation contact |  |  | Tier 3 | 0.26-9.99 | FERRARA | Other, see comment
FIPA_2023_1002_1536 | SCE-2133 |  | 2023-10-02 22:36 | Object contact | Animal contact |  | Non-HFTD | <3 meters of linear travel | CANBY | Other, see comment
FIPA_2023_1009_2057 | SCE-3001 | 129637889 | 2023-10-10 03:57 | Equipment failure |  | Connector device | Tier 2 | 0.26-9.99 | SKINNER | Other, see comment
FIPA_2023_1210_1113 | SCE-2944 | 129945500 | 2023-12-10 19:16 | Equipment failure |  | Transformer | Tier 3 | <0.25 | NERO | Other, see comment
FIPA_2023_1029_1810 | SCE-2355 | 129752757 | 2023-10-30 01:10 | Vandalism/theft |  |  | Non-HFTD | <3 meters of linear travel | NERO | Other, see comment
FIPA_2023_1115_0740 | SCE-2972 |  | 2023-11-15 15:40 | Vegetation contact |  |  | Non-HFTD | <0.25 | TEST | Other, see comment
FIPA_2023_1011_1400 | SCE-2972 | 129649112 | 2023-10-11 21:00 | Equipment failure |  | Connector device | Non-HFTD | <0.25 | TEST | Other, see comment
FIPA_2024_0303_2336 | SCE-3072 |  | 2024-03-04 07:36 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 | SAND CANYON | Covered
FIPA_2024_0309_0614 | SCE-2119 |  | 2024-03-09 14:14 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 |  | Other, see comment
FIPA_2024_0310_2232 | SCE-2175 | 130320952 | 2024-03-11 05:32 | Equipment failure |  | Anchor/guy | Tier 2 | <0.25 | CIRCLE | Other, see comment
FIPA_2024_0405_0840 | SCE-3296 | 130468727 | 2024-04-05 08:40 | Equipment failure |  | Conductor | Tier 2 | <0.25 | MORONGO | Other, see comment
FIPA_2024_0415_0320 | SCE-2185 | 130506014 | 2024-04-15 03:20 | Object contact | Other, see comment |  | Tier 2 | <0.25 | MIST | Other, see comment
FIPA_2024_0504_0858 | SCE-3331 | 130598297 | 2024-05-04 08:58 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | TANAGER | Covered
FIPA_2024_0516_0930 | SCE-3323 |  | 2024-05-16 09:30 | Object contact | Animal contact |  | Tier 3 | <0.25 | BOOTLEGGER | Covered
FIPA_2024_0523_1413 | SCE-2027 |  | 2024-05-23 14:13 | Equipment failure |  | Fuse | Tier 3 | <3 meters of linear travel | RAINBOW | Covered
FIPA_2024_0529_1724 | SCE-2970 | 130755492 | 2024-05-29 17:24 | Equipment failure |  | Connector device | Tier 2 | <0.25 | VENWIND 4 | Other, see comment
FIPA_2024_0604_1433 | SCE-3479 |  | 2024-06-04 14:33 | Vandalism/theft |  |  | Tier 2 | 0.26-9.99 | KINSEY | Covered
FIPA_2024_0626_0715 | SCE-2571 |  | 2024-06-26 07:15 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | CALIENTE | Other, see comment
FIPA_2024_0707_1515 | SCE-3076 |  | 2024-07-07 15:15 | Equipment failure |  | Pole | Tier 3 | <3 meters of linear travel | TECOLOTE | Other, see comment
FIPA_2024_0710_0011 | SCE-2648 |  | 2024-07-10 00:11 | Equipment failure |  | Splice | Tier 3 | <0.25 | LAMANDA | Other, see comment
FIPA_2024_0710_1059 | SCE-2327 |  | 2024-07-10 10:59 | Vegetation contact |  |  | Tier 2 | <0.25 | WOBEGONE | Covered
FIPA_2024_0718_1136 | SCE-3288 | 131007759 | 2024-07-18 11:36 | Vegetation contact |  |  | Tier 3 | <0.25 | THACHER | Covered
FIPA_2024_0718_2252 | SCE-2245 | 131009037 | 2024-07-18 22:52 | Object contact | Land vehicle contact |  | Tier 3 | <3 meters of linear travel | PICK | Covered
FIPA_2024_0723_1526 | SCE-2286 | 131032058 | 2024-07-23 15:26 | Object contact | Land vehicle contact |  | Tier 2 | <3 meters of linear travel | ELSTER | Other, see comment
FIPA_2024_0724_1320 | SCE-3350 |  | 2024-07-24 13:20 | Equipment failure |  | Splice | Tier 2 | <0.25 | MENIFEE | Covered
FIPA_2024_0727_1933 | SCE-3480 | 131054013 | 2024-07-27 19:33 | Equipment failure |  | Transformer | Tier 3 | 0.26-9.99 | HUGHES LAKE | Covered
FIPA_2024_0728_1243 | SCE-2752 |  | 2024-07-28 12:43 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | ROS | Other, see comment
FIPA_2024_0730_0000 | SCE-2142 |  | 2024-07-30 | Object contact | Animal contact |  | Tier 3 | <0.25 | COVENTRY | Other, see comment
FIPA_2024_0731_1330 | SCE-2599 | 131067902 | 2024-07-31 13:30 | Object contact | Balloon contact |  | Tier 2 | <0.25 | LOTTO | Covered
FIPA_2024_0801_1458 | SCE-2441 |  | 2024-08-01 14:58 | Wire-to-wire contact |  |  | Tier 2 | 0.26-9.99 | CUYAMA | Other, see comment
FIPA_2024_0815_0853_1 | SCE-2328 | 131146427 | 2024-08-15 08:53 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | INVADER | Other, see comment
FIPA_2024_0818_1730 | SCE-3735 |  | 2024-08-18 17:30 | Object contact | Balloon contact |  | Tier 3 | 0.26-9.99 | ANACONDA | Other, see comment
FIPA_2024_0823_0440 | SCE-2318 |  | 2024-08-23 04:40 | Vegetation contact |  |  | Tier 3 | 10-99 | TECOLOTE | Other, see comment
FIPA_2024_0827_1411 | SCE-2561 | 131197570 | 2024-08-27 14:11 | Equipment failure |  |  | Tier 3 | <0.25 | ANACONDA | Other, see comment
FIPA_2024_0829_1239 | SCE-2801 |  | 2024-08-29 12:39 | Equipment failure |  | Conductor | Tier 2 | <3 meters of linear travel | SHORELINE | Other, see comment
FIPA_2024_1010_1329 | SCE-2481 |  | 2024-10-10 13:29 | Lightning |  |  | Tier 3 | <0.25 | TAGGERT | Covered
FIPA_2024_1024_1529 | SCE-2646 |  | 2024-10-24 15:29 | Vegetation contact |  |  | Tier 2 | <0.25 | ANGELES | Other, see comment
FIPA_2024_1106_0830 | SCE-2353 |  | 2024-11-06 08:30 | Vegetation contact |  |  | Tier 3 | <0.25 | HOSS | Other, see comment
FIPA_2024_1109_1544 | SCE-2679 |  | 2024-11-09 15:44 | Equipment failure |  | Connector device | Tier 3 | 0.26-9.99 | PHEASANT | Covered
FIPA_2024_1201_0933 | SCE-2223 |  | 2024-12-01 09:33 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | CALGROVE | Covered

## HFTDIgnitionSummary
IgnitionID | NearestWeatherStationID | DoutageID | FireStartDateTime | SuspectedInitiatingCause | ObjectContact | EquipmentFailure | HFTDClass | FireSize | CircuitName | EquipmentType | LineClass | ConductorType | Cause
FIPA_2022_0211_1319 | SCE-2218 | 126504858 | 2022-02-11 13:19 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | <0.25 | Mulholland | Overhead | Primary Distribution | Bare | Vehicle
FIPA_2022_0204_1051 | SCE-2254 | 126471274 | 2022-02-04 10:51 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Rhoda | Overhead | Primary Distribution | Bare | Vegetation
FIPA_2022_0129_1000 | SCE-3035 | N/A | 2022-01-29 10:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Rhoda | Subsurface | Primary Distribution | Bare
FIPA_2022_0125_1512 | SCE-3045 | 126418206 | 2022-01-25 15:12 | Object contact | Vegetation contact | N/A | Tier 2 | <0.25 | Hurstview | Overhead | Primary Distribution | Bare
FIPA_2022_0422_0704 | SCE-2188 | 126827715 | 2022-04-22 07:04 | Equipment failure | N/A | Conductor | Tier 2 | <0.25 | Coachella | Overhead | Primary Distribution | Bare
FIPA_2022_0416_1457 | SCE-2573 |  | 2022-04-16 14:57 | Object contact | Balloon contact | N/A | Tier 3 | <0.25 | Huckleberry | Overhead | Primary Distribution | Bare | Balloon
FIPA_2022_0414_1242 | SCE-2192 |  | 2022-04-14 12:42 | Object contact | Animal contact | N/A | Tier 2 | 0.26-9.99 | St. Johns | Overhead | Primary Distribution | Bare | Animal
FIPA_2022_0413_1448 | SCE-2053 | 126787295 | 2022-04-13 14:48 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | 0.26-9.99 | Bidder | Overhead | Primary Distribution | Bare | Vehicle
FIPA_2022_0413_1830 | SCE-2053 | 126787295 | 2022-04-13 18:30 | Equipment failure | N/A | Switch | Tier 3 | <0.25 | Bidder | Overhead | Primary Distribution | Bare
FIPA_2022_0508_1456 | SCE-2300 |  | 2022-05-08 14:56 | Object contact | Animal contact | N/A | Tier 2 | <0.25 | Test | Overhead | Primary Distribution | Covered | Animal
FIPA_2022_0528_1053 | SCE-2261 |  | 2022-05-28 10:53 | Contamination | N/A | N/A | Tier 3 | 0.26-9.99 | Barrington | Overhead | Primary Distribution | Bare
FIPA_2022_0729_1803 | SCE-2148 | 127319918 | 2022-07-29 18:03 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Pancho | Subsurface | Primary Distribution | Bare
FIPA_2022_0824_1533 | SCE-2680 | N/A | 2022-08-24 15:33 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Pancho | Overhead | Primary Distribution | Bare | Animal
FIPA_2022_0901_1400 | SCE-2406 | 127502084 | 2022-09-01 14:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Crumner | Overhead | Primary Distribution | Other - see comment
FIPA_2022_0710_1953 | SCE-2255 | N/A | 2022-07-10 19:53 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Brennan | Overhead | Primary Distribution | Other - see comment | Animal
FIPA_2022_0904_1300 | SCE-2261 | 127522185 | 2022-09-04 13:00 | Equipment failure | N/A | Transformer | Tier 3 | <0.25 | Brennan | Subsurface | Primary Distribution | Other - see comment
FIPA_2022_0708_2245 | SCE-2063 | N/A | 2022-07-08 22:45 | Equipment failure | N/A | Conductor | Tier 3 | 0.26-9.99 | Stearns | Overhead | Primary Distribution | Bare
FIPA_2022_0807_1200 | SCE-2144 | N/A | 2022-08-07 12:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Stearns | Overhead | Primary Distribution | Bare
FIPA_2022_0819_1850 | N/A | N/A | 2022-08-19 18:50 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 |  | Overhead | Primary Distribution | Covered
FIPA_2022_0905_1650 | SCE-2633 | 127535002 | 2022-09-05 16:50 | Equipment failure | N/A | Connector device | Tier 2 | <0.25 | Grace | Subsurface | Primary Distribution | Bare
FIPA_2022_0909_1746 | SCE-2555 | 127573663 | 2022-09-09 17:46 | Equipment failure | N/A | Fuse | Tier 2 | <0.25 | Titan | Overhead | Primary Distribution | Covered
FIPA_2022_0717_1830 | SCE-2699 | 127253820 | 2022-07-17 18:30 | Equipment failure | N/A | Connector device | Tier 2 | <0.25 | Player | Subsurface | Primary Distribution | Bare
FIPA_2022_1002_1527 | SCE-2183 | 127714318 | 2022-10-02 15:27 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Trump | Overhead | Primary Distribution | Bare
FIPA_2022_1024_2107 | SCE-2203 | N/A | 2022-10-24 21:07 | Equipment failure | N/A | Splice/Clamp/Connector | Tier 3 | 0.26-9.99 | Red Mountain | Overhead | Primary Distribution | Bare
FIPA_2022_1116_1000 | SCE-2069 | 127988290 | 2022-11-16 10:00 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Vicasa | Overhead | Primary Distribution | Covered
FIPA_2022_1010_2243 | SCE-2840 | 127760724 | 2022-10-10 22:43 | Equipment failure | N/A | Transformer | Tier 2 | <0.25 | Interpace | Pad-mounted | Primary Distribution | Bare
FIPA_2022_1123_2229 | SCE-2274 | 128028617 | 2022-11-23 22:29 | Object contact | Vegetation contact | N/A | Tier 2 | 0.26-9.99 | Interpace | Overhead | Primary Distribution | Bare
FIPA_2023_0609_2119 | SCE-2809 | 129018104 | 2023-06-10 04:19 | Equipment failure |  | Connector device | Tier 3 | <0.25 | CANET | Overhead | Primary Distribution Line | Other, see comment
FIPA_2023_0804_1139 | SCE-2267 |  | 2023-08-04 18:39 | Equipment failure |  | Conductor | Tier 2 | <3 meters of linear travel | VERDEMONT | Subsurface | Secondary Distribution Line | Other, see comment
FIPA_2023_0715_1148 | SCE-2216 |  | 2023-07-15 18:48 | Equipment failure |  | Conductor | Tier 3 | <3 meters of linear travel | CLARINET | Overhead | Transmission Line | Other, see comment
FIPA_2023_0716_0103 | SCE-2216 | 129184852 | 2023-07-16 08:03 | Wire-to-wire contact |  |  | Tier 3 | <0.25 | CLARINET | Overhead | Primary Distribution Line | Other, see comment
FIPA_2023_0703_2112 | SCE-3010 | 129127716 | 2023-07-04 04:12 | Equipment failure |  | Connector device | Tier 2 | <3 meters of linear travel | WARDELL | Subsurface | Primary Distribution Line | Other, see comment
FIPA_2023_0815_1656 | SCE-2307 | 129328592 | 2023-08-15 23:56 | Equipment failure |  | Insulator and bushing | Tier 3 | <0.25 | GALAHAD | Overhead | Secondary Distribution Line | Covered
FIPA_2023_0712_1208 | SCE-2187 |  | 2023-07-12 19:08 | Object contact | Animal contact |  | Tier 3 | 0.26-9.99 | SALVADOR | Overhead | Transmission Line | Other, see comment | Animal
FIPA_2023_1029_1839 | SCE-2045 | 129753216 | 2023-10-30 01:39 | Equipment failure |  | Conductor | Tier 3 | <0.25 | ENERGY | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2023_1026_1644 | SCE-2932 | 129739482 | 2023-10-26 23:44 | Equipment failure |  | Other, see comment | Tier 3 | 0.26-9.99 | CONINE | Overhead | Primary Distribution Line | Covered
FIPA_2023_1030_0358 | SCE-2103 | 129754250 | 2023-10-30 10:58 | Vegetation contact |  |  | Tier 3 | 0.26-9.99 | FERRARA | Overhead | Primary Distribution Line | Other, see comment
FIPA_2023_1009_2057 | SCE-3001 | 129637889 | 2023-10-10 03:57 | Equipment failure |  | Connector device | Tier 2 | 0.26-9.99 | SKINNER | Overhead | Primary Distribution Line | Other, see comment
FIPA_2023_1210_1113 | SCE-2944 | 129945500 | 2023-12-10 19:16 | Equipment failure |  | Transformer | Tier 3 | <0.25 | NERO | Overhead | Primary Distribution Line | Other, see comment
FIPA_2024_0303_2336 | SCE-3072 |  | 2024-03-04 07:36 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 | SAND CANYON | Overhead | Primary Distribution Line | Covered | Vehicle
FIPA_2024_0309_0614 | SCE-2119 |  | 2024-03-09 14:14 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 |  | Overhead | Primary Distribution Line | Other, see comment | Vehicle
FIPA_2024_0310_2232 | SCE-2175 | 130320952 | 2024-03-11 05:32 | Equipment failure |  | Anchor/guy | Tier 2 | <0.25 | CIRCLE | Overhead | Primary Distribution Line | Covered
FIPA_2024_0405_0840 | SCE-3296 | 130468727 | 2024-04-05 08:40 | Equipment failure |  | Conductor | Tier 2 | <0.25 | MORONGO | Overhead | Primary Distribution Line | Other, see comment
FIPA_2024_0415_0320 | SCE-2185 | 130506014 | 2024-04-15 03:20 | Object contact | Other, see comment |  | Tier 2 | <0.25 | MIST | Overhead | Primary Distribution Line | Other, see comment | Other Contact
FIPA_2024_0504_0858 | SCE-3331 | 130598297 | 2024-05-04 08:58 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | TANAGER | Overhead | Primary Distribution Line | Covered | Animal
FIPA_2024_0516_0930 | SCE-3323 |  | 2024-05-16 09:30 | Object contact | Animal contact |  | Tier 3 | <0.25 | BOOTLEGGER | Overhead | Primary Distribution Line | Covered | Animal
FIPA_2024_0523_1413 | SCE-2027 |  | 2024-05-23 14:13 | Equipment failure |  | Fuse | Tier 3 | <3 meters of linear travel | RAINBOW | Overhead | Primary Distribution Line | Covered
FIPA_2024_0529_1724 | SCE-2970 | 130755492 | 2024-05-29 17:24 | Equipment failure |  | Connector device | Tier 2 | <0.25 | VENWIND 4 | Overhead | Primary Distribution Line | Other, see comment
FIPA_2024_0604_1433 | SCE-3479 |  | 2024-06-04 14:33 | Vandalism/theft |  |  | Tier 2 | 0.26-9.99 | KINSEY | Overhead | Secondary Distribution Line | Covered
FIPA_2024_0626_0715 | SCE-2571 |  | 2024-06-26 07:15 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | CALIENTE | Overhead | Secondary Distribution Line | Other, see comment | Animal
FIPA_2024_0707_1515 | SCE-3076 |  | 2024-07-07 15:15 | Equipment failure |  | Pole | Tier 3 | <3 meters of linear travel | TECOLOTE | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_0710_0011 | SCE-2648 |  | 2024-07-10 00:11 | Equipment failure |  | Splice | Tier 3 | <0.25 | LAMANDA | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_0710_1059 | SCE-2327 |  | 2024-07-10 10:59 | Vegetation contact |  |  | Tier 2 | <0.25 | WOBEGONE | Overhead | Secondary Distribution Line | Covered
FIPA_2024_0718_1136 | SCE-3288 | 131007759 | 2024-07-18 11:36 | Vegetation contact |  |  | Tier 3 | <0.25 | THACHER | Overhead | Primary Distribution Line | Covered
FIPA_2024_0718_2252 | SCE-2245 | 131009037 | 2024-07-18 22:52 | Object contact | Land vehicle contact |  | Tier 3 | <3 meters of linear travel | PICK | Overhead | Primary Distribution Line | Covered | Vehicle
FIPA_2024_0723_1526 | SCE-2286 | 131032058 | 2024-07-23 15:26 | Object contact | Land vehicle contact |  | Tier 2 | <3 meters of linear travel | ELSTER | Overhead | Primary Distribution Line | Other, see comment | Vehicle
FIPA_2024_0724_1320 | SCE-3350 |  | 2024-07-24 13:20 | Equipment failure |  | Splice | Tier 2 | <0.25 | MENIFEE | Overhead | Secondary Distribution Line | Covered
FIPA_2024_0727_1933 | SCE-3480 | 131054013 | 2024-07-27 19:33 | Equipment failure |  | Transformer | Tier 3 | 0.26-9.99 | HUGHES LAKE | Overhead | Primary Distribution Line | Covered
FIPA_2024_0728_1243 | SCE-2752 |  | 2024-07-28 12:43 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | ROS | Overhead | Primary Distribution Line | Other, see comment | Balloon
FIPA_2024_0730_0000 | SCE-2142 |  | 2024-07-30 | Object contact | Animal contact |  | Tier 3 | <0.25 | COVENTRY | Overhead | Primary Distribution Line | Other, see comment | Animal
FIPA_2024_0731_1330 | SCE-2599 | 131067902 | 2024-07-31 13:30 | Object contact | Balloon contact |  | Tier 2 | <0.25 | LOTTO | Overhead | Primary Distribution Line | Covered | Balloon
FIPA_2024_0801_1458 | SCE-2441 |  | 2024-08-01 14:58 | Wire-to-wire contact |  |  | Tier 2 | 0.26-9.99 | CUYAMA | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_0815_0853_1 | SCE-2328 | 131146427 | 2024-08-15 08:53 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | INVADER | Overhead | Primary Distribution Line | Other, see comment | Balloon
FIPA_2024_0818_1730 | SCE-3735 |  | 2024-08-18 17:30 | Object contact | Balloon contact |  | Tier 3 | 0.26-9.99 | ANACONDA | Overhead | Primary Distribution Line | Other, see comment | Balloon
FIPA_2024_0823_0440 | SCE-2318 |  | 2024-08-23 04:40 | Vegetation contact |  |  | Tier 3 | 10-99 | TECOLOTE | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_0827_1411 | SCE-2561 | 131197570 | 2024-08-27 14:11 | Equipment failure |  |  | Tier 3 | <0.25 | ANACONDA | Overhead | Primary Distribution Line | Other, see comment
FIPA_2024_0829_1239 | SCE-2801 |  | 2024-08-29 12:39 | Equipment failure |  | Conductor | Tier 2 | <3 meters of linear travel | SHORELINE | Overhead | Primary Distribution Line | Other, see comment
FIPA_2024_1010_1329 | SCE-2481 |  | 2024-10-10 13:29 | Lightning |  |  | Tier 3 | <0.25 | TAGGERT | Overhead | Primary Distribution Line | Covered
FIPA_2024_1024_1529 | SCE-2646 |  | 2024-10-24 15:29 | Vegetation contact |  |  | Tier 2 | <0.25 | ANGELES | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_1106_0830 | SCE-2353 |  | 2024-11-06 08:30 | Vegetation contact |  |  | Tier 3 | <0.25 | HOSS | Overhead | Secondary Distribution Line | Other, see comment
FIPA_2024_1109_1544 | SCE-2679 |  | 2024-11-09 15:44 | Equipment failure |  | Connector device | Tier 3 | 0.26-9.99 | PHEASANT | Overhead | Secondary Distribution Line | Covered
FIPA_2024_1201_0933 | SCE-2223 |  | 2024-12-01 09:33 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | CALGROVE | Overhead | Primary Distribution Line | Covered | Animal

## IgnOHPrimaryHFTD
IgnitionID | NearestWeatherStationID | DoutageID | FireStartDateTime | SuspectedInitiatingCause | ObjectContact | EquipmentFailure | HFTDClass | FireSize | CircuitName | EquipmentType | LineClass | ConductorType | ConductorCovered | Cause
FIPA_2022_0211_1319 | SCE-2218 | 126504858 | 2022-02-11 13:19 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | <0.25 | Mulholland | Overhead | Primary Distribution | Bare | Bare,Other | Vehicle
FIPA_2022_0204_1051 | SCE-2254 | 126471274 | 2022-02-04 10:51 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Rhoda | Overhead | Primary Distribution | Bare | Bare,Other | Vegetation
FIPA_2022_0125_1512 | SCE-3045 | 126418206 | 2022-01-25 15:12 | Object contact | Vegetation contact | N/A | Tier 2 | <0.25 | Hurstview | Overhead | Primary Distribution | Bare | Bare,Other | Vegetation
FIPA_2022_0422_0704 | SCE-2188 | 126827715 | 2022-04-22 07:04 | Equipment failure | N/A | Conductor | Tier 2 | <0.25 | Coachella | Overhead | Primary Distribution | Bare | Bare,Other | Conductor
FIPA_2022_0416_1457 | SCE-2573 |  | 2022-04-16 14:57 | Object contact | Balloon contact | N/A | Tier 3 | <0.25 | Huckleberry | Overhead | Primary Distribution | Bare | Bare,Other | Balloon
FIPA_2022_0414_1242 | SCE-2192 |  | 2022-04-14 12:42 | Object contact | Animal contact | N/A | Tier 2 | 0.26-9.99 | St. Johns | Overhead | Primary Distribution | Bare | Bare,Other | Animal
FIPA_2022_0413_1448 | SCE-2053 | 126787295 | 2022-04-13 14:48 | Object contact | Vehicle contact - car pole | N/A | Tier 3 | 0.26-9.99 | Bidder | Overhead | Primary Distribution | Bare | Bare,Other | Vehicle
FIPA_2022_0413_1830 | SCE-2053 | 126787295 | 2022-04-13 18:30 | Equipment failure | N/A | Switch | Tier 3 | <0.25 | Bidder | Overhead | Primary Distribution | Bare | Bare,Other | Switch
FIPA_2022_0508_1456 | SCE-2300 |  | 2022-05-08 14:56 | Object contact | Animal contact | N/A | Tier 2 | <0.25 | Test | Overhead | Primary Distribution | Covered | Covered | Animal
FIPA_2022_0528_1053 | SCE-2261 |  | 2022-05-28 10:53 | Contamination | N/A | N/A | Tier 3 | 0.26-9.99 | Barrington | Overhead | Primary Distribution | Bare | Bare,Other | Contamination
FIPA_2022_0824_1533 | SCE-2680 | N/A | 2022-08-24 15:33 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Pancho | Overhead | Primary Distribution | Bare | Bare,Other | Animal
FIPA_2022_0901_1400 | SCE-2406 | 127502084 | 2022-09-01 14:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Crumner | Overhead | Primary Distribution | Other - see comment | Bare,Other | Conductor
FIPA_2022_0710_1953 | SCE-2255 | N/A | 2022-07-10 19:53 | Object contact | Animal contact | N/A | Tier 3 | <0.25 | Brennan | Overhead | Primary Distribution | Other - see comment | Bare,Other | Animal
FIPA_2022_0708_2245 | SCE-2063 | N/A | 2022-07-08 22:45 | Equipment failure | N/A | Conductor | Tier 3 | 0.26-9.99 | Stearns | Overhead | Primary Distribution | Bare | Bare,Other | Conductor
FIPA_2022_0807_1200 | SCE-2144 | N/A | 2022-08-07 12:00 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Stearns | Overhead | Primary Distribution | Bare | Bare,Other | Conductor
FIPA_2022_0819_1850 | N/A | N/A | 2022-08-19 18:50 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 |  | Overhead | Primary Distribution | Covered | Covered | Conductor
FIPA_2022_0909_1746 | SCE-2555 | 127573663 | 2022-09-09 17:46 | Equipment failure | N/A | Fuse | Tier 2 | <0.25 | Titan | Overhead | Primary Distribution | Covered | Covered | Fuse
FIPA_2022_1002_1527 | SCE-2183 | 127714318 | 2022-10-02 15:27 | Equipment failure | N/A | Conductor | Tier 3 | <0.25 | Trump | Overhead | Primary Distribution | Bare | Bare,Other | Conductor
FIPA_2022_1024_2107 | SCE-2203 | N/A | 2022-10-24 21:07 | Equipment failure | N/A | Splice/Clamp/Connector | Tier 3 | 0.26-9.99 | Red Mountain | Overhead | Primary Distribution | Bare | Bare,Other | Splice
FIPA_2022_1116_1000 | SCE-2069 | 127988290 | 2022-11-16 10:00 | Object contact | Vegetation contact | N/A | Tier 3 | <0.25 | Vicasa | Overhead | Primary Distribution | Covered | Covered | Vegetation
FIPA_2022_1123_2229 | SCE-2274 | 128028617 | 2022-11-23 22:29 | Object contact | Vegetation contact | N/A | Tier 2 | 0.26-9.99 | Interpace | Overhead | Primary Distribution | Bare | Bare,Other | Vegetation
FIPA_2023_0609_2119 | SCE-2809 | 129018104 | 2023-06-10 04:19 | Equipment failure |  | Connector device | Tier 3 | <0.25 | CANET | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Connector Device
FIPA_2023_0716_0103 | SCE-2216 | 129184852 | 2023-07-16 08:03 | Wire-to-wire contact |  |  | Tier 3 | <0.25 | CLARINET | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Wire-to-Wire
FIPA_2023_1026_1644 | SCE-2932 | 129739482 | 2023-10-26 23:44 | Equipment failure |  | Other, see comment | Tier 3 | 0.26-9.99 | CONINE | Overhead | Primary Distribution Line | Covered | Covered | Equipment - Other
FIPA_2023_1030_0358 | SCE-2103 | 129754250 | 2023-10-30 10:58 | Vegetation contact |  |  | Tier 3 | 0.26-9.99 | FERRARA | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Vegetation
FIPA_2023_1009_2057 | SCE-3001 | 129637889 | 2023-10-10 03:57 | Equipment failure |  | Connector device | Tier 2 | 0.26-9.99 | SKINNER | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Connector Device
FIPA_2023_1210_1113 | SCE-2944 | 129945500 | 2023-12-10 19:16 | Equipment failure |  | Transformer | Tier 3 | <0.25 | NERO | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Transformer
FIPA_2024_0303_2336 | SCE-3072 |  | 2024-03-04 07:36 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 | SAND CANYON | Overhead | Primary Distribution Line | Covered | Covered | Vehicle
FIPA_2024_0309_0614 | SCE-2119 |  | 2024-03-09 14:14 | Object contact | Land vehicle contact |  | Tier 3 | <0.25 |  | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Vehicle
FIPA_2024_0310_2232 | SCE-2175 | 130320952 | 2024-03-11 05:32 | Equipment failure |  | Anchor/guy | Tier 2 | <0.25 | CIRCLE | Overhead | Primary Distribution Line | Covered | Covered | Anchor/Guy
FIPA_2024_0405_0840 | SCE-3296 | 130468727 | 2024-04-05 08:40 | Equipment failure |  | Conductor | Tier 2 | <0.25 | MORONGO | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Conductor
FIPA_2024_0415_0320 | SCE-2185 | 130506014 | 2024-04-15 03:20 | Object contact | Other, see comment |  | Tier 2 | <0.25 | MIST | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Other Contact
FIPA_2024_0504_0858 | SCE-3331 | 130598297 | 2024-05-04 08:58 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | TANAGER | Overhead | Primary Distribution Line | Covered | Covered | Animal
FIPA_2024_0516_0930 | SCE-3323 |  | 2024-05-16 09:30 | Object contact | Animal contact |  | Tier 3 | <0.25 | BOOTLEGGER | Overhead | Primary Distribution Line | Covered | Covered | Animal
FIPA_2024_0523_1413 | SCE-2027 |  | 2024-05-23 14:13 | Equipment failure |  | Fuse | Tier 3 | <3 meters of linear travel | RAINBOW | Overhead | Primary Distribution Line | Covered | Covered | Fuse
FIPA_2024_0529_1724 | SCE-2970 | 130755492 | 2024-05-29 17:24 | Equipment failure |  | Connector device | Tier 2 | <0.25 | VENWIND 4 | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Connector Device
FIPA_2024_0718_1136 | SCE-3288 | 131007759 | 2024-07-18 11:36 | Vegetation contact |  |  | Tier 3 | <0.25 | THACHER | Overhead | Primary Distribution Line | Covered | Covered | Vegetation
FIPA_2024_0718_2252 | SCE-2245 | 131009037 | 2024-07-18 22:52 | Object contact | Land vehicle contact |  | Tier 3 | <3 meters of linear travel | PICK | Overhead | Primary Distribution Line | Covered | Covered | Vehicle
FIPA_2024_0723_1526 | SCE-2286 | 131032058 | 2024-07-23 15:26 | Object contact | Land vehicle contact |  | Tier 2 | <3 meters of linear travel | ELSTER | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Vehicle
FIPA_2024_0727_1933 | SCE-3480 | 131054013 | 2024-07-27 19:33 | Equipment failure |  | Transformer | Tier 3 | 0.26-9.99 | HUGHES LAKE | Overhead | Primary Distribution Line | Covered | Covered | Transformer
FIPA_2024_0728_1243 | SCE-2752 |  | 2024-07-28 12:43 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | ROS | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Balloon
FIPA_2024_0730_0000 | SCE-2142 |  | 2024-07-30 | Object contact | Animal contact |  | Tier 3 | <0.25 | COVENTRY | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Animal
FIPA_2024_0731_1330 | SCE-2599 | 131067902 | 2024-07-31 13:30 | Object contact | Balloon contact |  | Tier 2 | <0.25 | LOTTO | Overhead | Primary Distribution Line | Covered | Covered | Balloon
FIPA_2024_0815_0853_1 | SCE-2328 | 131146427 | 2024-08-15 08:53 | Object contact | Balloon contact |  | Tier 2 | 0.26-9.99 | INVADER | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Balloon
FIPA_2024_0818_1730 | SCE-3735 |  | 2024-08-18 17:30 | Object contact | Balloon contact |  | Tier 3 | 0.26-9.99 | ANACONDA | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Balloon
FIPA_2024_0827_1411 | SCE-2561 | 131197570 | 2024-08-27 14:11 | Equipment failure |  |  | Tier 3 | <0.25 | ANACONDA | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Equipment - Other
FIPA_2024_0829_1239 | SCE-2801 |  | 2024-08-29 12:39 | Equipment failure |  | Conductor | Tier 2 | <3 meters of linear travel | SHORELINE | Overhead | Primary Distribution Line | Other, see comment | Bare,Other | Conductor
FIPA_2024_1010_1329 | SCE-2481 |  | 2024-10-10 13:29 | Lightning |  |  | Tier 3 | <0.25 | TAGGERT | Overhead | Primary Distribution Line | Covered | Covered | Lightnimg
FIPA_2024_1201_0933 | SCE-2223 |  | 2024-12-01 09:33 | Object contact | Animal contact |  | Tier 3 | <3 meters of linear travel | CALGROVE | Overhead | Primary Distribution Line | Covered | Covered | Animal