## README
Did not receive the same self-consistent sets of data from SCE this year and instead had to cobble them together from existing pieces.
The SCE GRC provided the last internally consistent data set 2-1.a-f_MGRA-SCE-002_Q2-CCUG-WD-Ign-jwm.xlsx can be found in the SCEGRC25 Workpapers.
The data sets received this year either looked at "cirucuits that are only CC" and the rest as partial, or "fully bare circuits" and the rest as partial.
Worse, it seems they were associating ignitions and WDs with the "partial" set and made no effort to attibute them to the segment.
I performed this anaysls myself using the SCE GRC GIS data.
1) I selected the line segments that were associated with ignitions and create a layer from them.
2) I merged this layer with the ignitions and created a new ignition segment, which now had CC/bare information.
3) I screened the data for how I understand 'reportabiltiy' to work - No self-extingusihing fires or those less than .3 m.
4) I applied further screens for "Primary" circuit and for HFTD location.
5) I extracted data into an excel spreadsheet, which forms the basis of the ignition data in this document for 2024. For 2019-2023 I rely on SCE's previous filings.
The file MGRA-SCE-003 Q1-Full-CC-WD-Ign-24-jwm contains alternative information: "Number of miles of fully covered conductor HFRA circuits" and "Number of fully "bare wire" HFRA circuits.
The mileages for these add up to a much smaller number than seen on the Miles Installed page, because most circuits are not "full" this or "fully" that.
Additionally we know some undergrounding and line removal is being done so these will subtract from the total. Howerver, this is not shown in Line 4 of the Miles Installed page, which shows a constant.
We can make some assumptions and derive our own mileage number fully bare circuit
1) SCE knows how many miles of CC it has deployed, so these are good numbers.
2) SCE knows how many miles of fully bare wire it has deployed. These are good numbers.
3) We can then imput a number that shows the reduced bare wire from removal and undergrounding which is ALL-CC+FullBare
However things don't add up so need to supplement with real UG / WR numbers.
Recalculation after receipt of DRR MGRA-SCE-007-2
This DR asked for validation of the list, and SCE provided additional ignitions.
Source of differences: 1) definition of reportable - if self-extinguished or <3 ft may not be reportable, SCE reported these to CPUC. 2) 5 ignitions are not in the GIS data reported to OEIS, 3) 3 events were not in HFTD.
New calculations include SE/small fires, but not unreported or non-HFTD.
Tab Ignitions_SCE_DR6-7 applies SCE's 2024 methodology to historical ignitions for its HFRA.

## Miles Installed
| 2019 | 2020 | 2021 | 2022 | 2023 | 2024
Bare Miles | 8952 | 7992 | 6492 | 5093 | 3873 | 3077
CC installed miles | 372 | 1332 | 2832 | 4231 | 5451 | 6247
Total | 9324 | 9324 | 9324 | 9324 | 9324 | 9324
Fully Bare Circuits | 8494 | 5794 | 3926 | 2467 | 1258 | 1004
Fully CC Circuits | 0 | 380 | 451 | 649 | 1043 | 1258
Partial CC | 372 | 952 | 2381 | 3582 | 4408 | 4989
Bare + UG + RW | 8952 | 7992 | 6492 | 5093 | 3873 | 3077
Imputed UG + WR | 458 | 2198 | 2566 | 2626 | 2615 | 2073
Effective Bare Miles | 8952 | 7126 | 6758 | 6698 | 6709 | 7251
BW Weight of mi/yr | 0.25232 | 0.22526 | 0.18298 | 0.14355 | 0.10916 | 0.086727 | 1
CC Weight of mi/yr | 0.018177 | 0.065087 | 0.13838 | 0.20674 | 0.26636 | 0.30525 | 1

## Wire Downs
| 2019 | 2020 | 2021 | 2022 | 2023 | Total or Wtd Avg
Bare Wire Downs | 218 | 166 | 162 | 121 | 189 | 856
Covered Conductor Wire Downs | 2 | 2 | 19 | 29 | 76 | 128
BW Wire Downs / mile-yr | 0.024352 | 0.020771 | 0.024954 | 0.023758 | 0.048799 | 0.024127
CC Wire Downs / mile-yr | 0.0053763 | 0.0015015 | 0.006709 | 0.0068542 | 0.013942 | 0.0062546
BW / CC | 4.5295 | 13.8333 | 3.7194 | 3.4662 | 3.5001 | 3.8575
Reduction % | 77.92% | 92.77% | 73.11% | 71.15% | 71.43% | 74.08%
Expected CC Wires Down | 9.059 | 27.6667 | 70.6691 | 100.5205 | 266.0054 | 473.9207

## Ignitions_current
Calculations | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Total or Wtd Avg | 95% CL (1 tail) | 90% CL (1 tail) | 1 sigma
Bare Wire Reportable Ignitions | 37 | 49 | 46 | 36 | 15 | 12 | 195
Covered Conductor Reportable Ignitions | 0 | 1 | 2 | 5 | 3 | 10 | 21 | 30.2404 | 28.1843 | 23.9153
BW Ignitions / mile-yr | 0.0041332 | 0.0061311 | 0.0070856 | 0.0070685 | 0.003873 | 0.0038999 | 0.0054962
CC Ignitions / mile-yr | 0 | 0.00075075 | 0.00070621 | 0.0011818 | 0.00055036 | 0.0016008 | 0.0010261
BW / CC |  | 8.1667 | 10.0333 | 5.9814 | 7.0372 | 2.4363 | 5.3562
Reduction % |  | 87.76% | 90.03% | 83.28% | 85.79% | 58.95% | 81.33% | 62.57% | 65.11% | 70.4%
Expected CC ignitions | 1.5375 | 8.1667 | 20.0665 | 29.9069 | 21.1115 | 24.3627 | 80.7892

## Ignitions_SCE_DR6-7
Calculations | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | Total or Wtd Avg
Bare Wire Reportable Ignitions | 38 | 31 | 25 | 23 | 9 | 16 | 142
Covered Conductor Reportable Ignitions | 0 | 1 | 2 | 3 | 2 | 13 | 21
BW Ignitions / mile-yr | 0.0042449 | 0.0038789 | 0.0038509 | 0.004516 | 0.0023238 | 0.0051999 | 0.0040024
CC Ignitions / mile-yr | 0 | 0.00075075 | 0.00070621 | 0.00070905 | 0.00036691 | 0.002081 | 0.0010261
BW / CC |  | 5.1667 | 5.4529 | 6.3691 | 6.3335 | 2.4987 | 3.9004
Reduction % |  | 80.65% | 81.66% | 84.3% | 84.21% | 59.98% | 74.36%
Expected CC ignitions | 1.5791 | 5.1667 | 10.9057 | 19.1072 | 12.6669 | 32.4836 | 49.4256

## CL Stats
Events | 95% CL (1 tail) | 90% CL (1 tail) | 1 sigma | WD 95% CL
0 | 2.9957 | 2.3026 | 1.1394 | 56.25%
1 | 4.7439 | 3.8897 | 2.3477
2 | 6.2958 | 5.3223 | 3.5046
3 | 7.7537 | 6.6808 | 4.6352
4 | 9.1535 | 7.9936 | 5.7494
5 | 10.513 | 9.2747 | 6.8521
6 | 11.8424 | 10.5321 | 7.9461
7 | 13.1481 | 11.7709 | 9.0334
8 | 14.4346 | 12.9947 | 10.1152
9 | 15.7052 | 14.206 | 11.1924
10 | 16.9622 | 15.4066 | 12.2657
11 | 18.2075 | 16.5981 | 13.3357
12 | 19.4426 | 17.7816 | 14.4028
13 | 20.6686 | 18.958 | 15.4672
14 | 21.8865 | 20.128 | 16.5294
15 | 23.0971 | 21.2924 | 17.5894
16 | 24.3012 | 22.4516 | 18.6476
17 | 25.4992 | 23.6061 | 19.704
18 | 26.6918 | 24.7563 | 20.7589
19 | 27.8792 | 25.9025 | 21.8123
20 | 29.062 | 27.0451 | 22.8644
21 | 30.2404 | 28.1843 | 23.9153
22 | 31.4148 | 29.3203 | 24.965