## Data
LineClass | Primary Distribution Line
Reportable | 1
Row Labels | Count of ConductorType
Covered | 4
Other, see comment | 8
Grand Total | 12

## SCE_Ignitions_Lines
OBJECTID_12 | OBJECTID | IgnitionID | UtilityID | SubstationID | NearestWeatherStationID | OutageID | FireStartDateTime | FireStartYear | FireDetectionMethod | FireDetectionMethodComment | SuspectedInitiatingCause | SuspectedInitiatingCauseComment | ObjectContact | ObjectContactComment | VegetationGenus | VegetationSpecies | VegetationCommonName | EquipmentFailure | EquipmentFailureComment | AssociatedNominalVoltagekV | AssociatedOperatingVoltagekV | EquipmentType | Determination | DeterminationComment | FacilityContacted | FacilityContactedComment | AssetID | AssetFeature | SegmentID | CircuitID | LineClass | ContributingFactor | ContributingFactorComment | RFWStatus | RFWIssueDateTime | FWWStatus | FWWIssueDateTime | HWWStatus | HWWIssueDateTime | OriginLandUse | MaterialAtOrigin | MaterialAtOriginComment | FuelBedDescription | FuelBedDescriptionComment | FireSize | SuppressedBy | SuppressingAgency | FireInvestigation | FireAHJ | IgnitionNotes | HFTDClass | OBJECTID_1 | SegmentID_1 | CircuitID_1 | UtilityID_1 | SubstationID_1 | CircuitName | ConductorType | ConductorTypeComment | AssetOHUG | NominalVoltagekV | OperatingVoltagekV | SubstationName | ConductorMaterial | ConductorMaterialComment | ConductorSize | ConductorOD | LastInspectionDate | LastMaintenanceDate | InstallationDate | InstallationYear | EstimatedAge | UsefulLifespan | AmpacityRating | Distance | Reportable
3 | 5 | FIPA_2024_0303_2336 | SCE | ES-5560 | SCE-3072 |  | 2024-03-04 07:36 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Support structure |  | OH-1790725E | Support Structure |  | ED-15737 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Other, see comment | Car | Fire-resistive fuel bed |  | <0.25 | Fire agency | Los Angeles County FD | No |  |  | Tier 3 | 801917 | 309636716 | ED-15737 | SCE | ES-5560 | SAND CANYON | Covered |  | Overhead | 16 |  | Solemint | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 2022-05-20 | 2022 | 0-9 |  |  | 3.1666 | 1
1 | 7 | FIPA_2024_0309_0614 | SCE | ES-8096 | SCE-2119 |  | 2024-03-09 14:14 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | OH-83182E | Support Structure |  | ED-15986 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Structure |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Local FD | No |  |  | Tier 3 | 522569 | 84008346 |  | SCE |  |  | Other, see comment |  | Overhead |  |  |  | Other, see comment | [10 empty] | 3.2665 | 1
2 | 8 | FIPA_2024_0310_2232 | SCE | ED-8318 | SCE-2175 | 130320952 | 2024-03-11 05:32 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Anchor/guy |  | 12 | 12 | Overhead | Utility personnel |  |  |  | OH-2341991E | Support Structure |  | ED-03519 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino FD | No |  |  | Tier 2 | 640311 | 81977481 | ED-03519 | SCE | ED-8318 | CIRCLE | Other, see comment | A | Overhead | 12 |  | OAK SPRINGS P.T. | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 2.9864 | 1
6 | 1 | FIPA_2024_0405_0840 | SCE | ED-7549 | SCE-3296 | 130468727 | 2024-04-05 08:40 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-12178 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Structure |  | Brush fuel model |  | <0.25 | Fire agency | San Bernardino County Fire Dep | No |  |  | Tier 2 | 865487 | 335229954 | ED-12178 | SCE | ED-7549 | MORONGO | Other, see comment | A | Overhead | 12 |  | MORONGO P.T. | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2022-03-07 | 2022 | 0-9 |  |  | 3.0451 | 1
10 | 19 | FIPA_2024_0415_0320 | SCE | ES-5372 | SCE-2185 | 130506014 | 2024-04-15 03:20 | 2024 | Utility staff |  | Object contact |  | Other, see comment | Inconclusive | [5 empty] | 16 | 16 | Overhead | Utility personnel |  | Conductor: Primary |  | 4743368E-205664653 | Support Structure |  | ED-12011 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 1045279 | 10516129 | ED-12011 | SCE | ES-5372 | MIST | Other, see comment | C | Overhead | 16 |  | Capitan | Other, see comment | C | 2/0 | [8 empty] | 2.5511 | FALSE
4 | 2 | FIPA_2024_0504_0858 | SCE | ES-5380 | SCE-3331 | 130598297 | 2024-05-04 08:58 | 2024 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Transformer |  | 0 | Support Structure |  | ED-17529 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Tier 3 | 215897 | 312056952 | ED-17529 | SCE | ES-5380 | TANAGER | Covered |  | Overhead | 12 |  | BANDUCCI | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-11-01 | 2019 | 0-9 |  |  | 1.1192 | FALSE
5 | 28 | FIPA_2024_0516_0930 | SCE | ES-5365 | SCE-3323 |  | 2024-05-16 09:30 | 2024 | Utility staff |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Transformer |  | 0 | Support Structure |  | ED-01954 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Utility |  | No |  |  | Tier 3 | 708585 | 312787117 | ED-01954 | SCE | ES-5365 | BOOTLEGGER | Covered |  | Overhead | 12 |  | Acton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 3.0681 | 1
8 | 8 | FIPA_2024_0523_1413 | SCE | ES-5536 | SCE-2027 |  | 2024-05-23 14:13 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Fuse |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-14645 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <3 meters of linear travel | Self-extinguished |  | No |  |  | Tier 3 | 910663 | 10493193 | ED-14645 | SCE | ES-5536 | RAINBOW | Covered |  | Overhead | 16 |  | Somis | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-06-02 | 2021 | 0-9 |  |  | 2.5569 | FALSE
7 | 25 | FIPA_2024_0529_1724 | SCE | ES-8306 | SCE-2970 | 130755492 | 2024-05-29 17:24 | 2024 | Utility staff |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-21194 | Primary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 875988 | 88589744 | ED-21194 | SCE | ES-8306 | VENWIND 4 | Other, see comment | A | Overhead | 12 |  | Venwind | Aluminum conductor steel reinforced (ACSR) |  | 653 | [8 empty] | 3.0805 | FALSE
11 | 9 | FIPA_2024_0604_1433 | SCE | ES-5512 | SCE-3479 |  | 2024-06-04 14:33 | 2024 | Fire agency |  | Vandalism/theft | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-09777 | Secondary Distribution Line | Unknown |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | U.S. Forest Service | No |  |  | Tier 2 | 1156434 | 10531368 | ED-09777 | SCE | ES-5512 | KINSEY | Covered |  | Overhead | 12 |  | Gorman | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 3.2053 | 1
9 | 5 | FIPA_2024_0626_0715 | SCE |  | SCE-2571 |  | 2024-06-26 07:15 | 2024 |  |  | Object contact |  | Animal contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Splice/clamp/connector |  | 0 | Support Structure |  |  | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban |  |  | Other, see comment | Minor Roads surrounded by Low FB fuel | <3 meters of linear travel | Fire agency | KERN COUNTY FD_NONE | No |  |  | Tier 3 | 947032 | 73692637 | ED-02680 | SCE | ES-5357 | CALIENTE | Other, see comment | A | Overhead | 12 |  | Cummings | Aluminum conductor steel reinforced (ACSR) |  | 4 |  |  |  | 2022-08-11 | 2022 | 0-9 |  |  | 3.1908 | FALSE
14 | 8 | FIPA_2024_0707_1515 | SCE | ES-5570 | SCE-3076 |  | 2024-07-07 15:15 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Pole |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 1286521E-201831050 | Support Structure |  | ED-17605 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Santa Barbara Fire Department | No |  |  | Tier 3 | 192850 | 10521047 | ED-17605 | SCE | ES-5570 | TECOLOTE | Other, see comment | A | Overhead | 16 |  | Vegas | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 3.0784 | FALSE
26 | 44 | FIPA_2024_0710_0011 | SCE | ES-5115 | SCE-2648 |  | 2024-07-10 00:11 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Splice |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 4614792E-202006041 | Support Structure |  | ED-10020 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 674629 | 133930338 | ED-10020 | SCE | ES-5115 | LAMANDA | Other, see comment | A | Overhead | 16 |  | Eaton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 3.0465 | 1
18 | 50 | FIPA_2024_0710_1059 | SCE | ES-8056 | SCE-2327 |  | 2024-07-10 10:59 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-19586 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 380105 | 337674503 | ED-19586 | SCE | ES-8056 | WOBEGONE | Covered |  | Overhead | 12 |  | LAKEVIEW | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-11-29 | 2021 | 0-9 |  |  | 3.1634 | 1
17 | 21 | FIPA_2024_0718_1136 | SCE | ES-5526 | SCE-3288 | 131007759 | 2024-07-18 11:36 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 4863233E-207633728 | Support Structure |  | ED-17731 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 379425 | 309085482 | ED-17731 | SCE | ES-5526 | THACHER | Covered |  | Overhead | 16 |  | Ojai | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2019-01-01 | 2019 | 0-9 |  |  | 2.9043 | 1
15 | 27 | FIPA_2024_0718_2252 | SCE | ES-5365 | SCE-2245 | 131009037 | 2024-07-18 22:52 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | 4429426E-205706899 | Support Structure |  | ED-14047 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 276998 | 312913703 | ED-14047 | SCE | ES-5365 | PICK | Covered |  | Overhead | 12 |  | Acton | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-05-16 | 2021 | 0-9 |  |  | 3.0474 | FALSE
23 | 51 | FIPA_2024_0723_1526 | SCE | ES-5351 | SCE-2286 | 131032058 | 2024-07-23 15:26 | 2024 | Fire agency |  | Object contact |  | Land vehicle contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Support structure |  | 0 | Support Structure |  | ED-05850 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Tulare County Fire Department | No |  |  | Tier 2 | 601797 | 67614993 | ED-05850 | SCE | ES-5351 | ELSTER | Other, see comment | C | Overhead | 12 |  | Boxwood | Other, see comment | C | 6 | [8 empty] | 3.0483 | FALSE
19 | 10 | FIPA_2024_0724_1320 | SCE | ES-8342 | SCE-3350 |  | 2024-07-24 13:20 | 2024 | Public |  | Equipment failure | [6 empty] | Splice |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 4978055E-250029539 | Support Structure |  | ED-11058 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Grass fuel model |  | <0.25 | Customer |  | No |  |  | Tier 2 | 454490 | 344422477 | ED-11058 | SCE | ES-8342 | MENIFEE | Covered |  | Overhead | 12 |  | Newcomb | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 2022-09-14 | 2022 | 0-9 |  |  | 3.122 | 1
20 | 22 | FIPA_2024_0727_1933 | SCE | ES-5508 | SCE-3480 | 131054013 | 2024-07-27 19:33 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Transformer |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 709052E-208285916 | Support Structure |  | ED-08810 | Primary Distribution Line | Weather |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 506736 | 10553284 | ED-08810 | SCE | ES-5508 | HUGHES LAKE | Covered |  | Overhead | 12 |  | Del Sur | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 2.8434 | 1
24 | 28 | FIPA_2024_0728_1243 | SCE | ES-5070 | SCE-2752 |  | 2024-07-28 12:43 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Conductor: Primary |  | 312510S-200821631 | Support Structure |  | ED-06504 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 630765 | 120266107 | ED-06504 | SCE | ES-5070 | ROS | Other, see comment | A | Overhead | 12 |  | Valley | Aluminum conductor steel reinforced (ACSR) |  | 336 | [8 empty] | 5.1484 | 1
13 | 40 | FIPA_2024_0730_0000 | SCE | ES-5569 | SCE-2142 |  | 2024-07-30 | 2024 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-04226 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 120387 | 346302433 | ED-04226 | SCE | ES-5569 | COVENTRY | Other, see comment | A | Overhead | 16 |  | Thousand Oaks | Aluminum conductor steel reinforced (ACSR) |  | 4/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 7.1992 | 1
12 | 52 | FIPA_2024_0731_1330 | SCE | ES-8010 | SCE-2599 | 131067902 | 2024-07-31 13:30 | 2024 | Utility staff |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Fuse |  | 0 | Support Structure |  | ED-10735 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 2 | 102277 | 81988088 | ED-10735 | SCE | ES-8010 | LOTTO | Covered |  | Overhead | 12 |  | Phelan | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 3.2453 | FALSE
28 | 58 | FIPA_2024_0801_1458 | SCE | EX-4135 | SCE-2441 |  | 2024-08-01 14:58 | 2024 | Fire agency |  | Wire-to-wire contact | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 851612E-201781968 | Support Structure |  | ED-04540 | Secondary Distribution Line |  |  | Yes | 2024-08-01 19:00 | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Ventura County Fire Department | No |  |  | Tier 2 | 754113 | 345416467 | ED-04540 | SCE | EX-4135 | CUYAMA | Other, see comment | UNKNOWN | Overhead | 12 |  | TAFT | Other, see comment | UNKNOWN | UNKNOWN |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 3.2464 | 1
27 | 41 | FIPA_2024_0815_0853_1 | SCE | ES-5067 | SCE-2328 | 131146427 | 2024-08-15 08:53 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 12 | 12 | Overhead | Utility personnel |  | Insulator |  | 0 | Support Structure |  | ED-08946 | Primary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 2 | 734827 | 88589662 | ED-08946 | SCE | ES-5067 | INVADER | Other, see comment | A | Overhead | 12 |  | Devers | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 3.0061 | 1
22 | 59 | FIPA_2024_0818_1730 | SCE | ES-5546 | SCE-3735 |  | 2024-08-18 17:30 | 2024 | Fire agency |  | Object contact |  | Balloon contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Insulator |  | 589097E-208564453 | Support Structure |  | ED-07742 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 0.26-9.99 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 554524 | 347344868 | ED-00484 | SCE | ES-5542 | ANACONDA | Other, see comment | A | Overhead | 16 |  | North Oaks | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 49085.8139 | 1
25 | 18 | FIPA_2024_0823_0440 | SCE | ES-5372 | SCE-2318 |  | 2024-08-23 04:40 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 807731E-201916856 | Support Structure |  | ED-12011 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Brush fuel model |  | 10-99 | Fire agency | Santa Barbara County Fire Depa | No |  |  | Tier 3 | 667562 | 10524446 | ED-17605 | SCE | ES-5570 | TECOLOTE | Other, see comment | A | Overhead | 16 |  | Vegas | Aluminum conductor steel reinforced (ACSR) |  | 4 | [8 empty] | 72800.2021 | 1
21 | 48 | FIPA_2024_0827_1411 | SCE | ES-5542 | SCE-2561 | 131197570 | 2024-08-27 14:11 | 2024 | Fire agency |  | Equipment failure | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 4081329E-202213667 | Support Structure |  | ED-00484 | Primary Distribution Line |  |  | No |  | No |  | No |  | Urban | Vegetation |  | Timber fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 554524 | 347344868 | ED-00484 | SCE | ES-5542 | ANACONDA | Other, see comment | A | Overhead | 16 |  | North Oaks | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 7.2518 | 1
16 | 54 | FIPA_2024_0829_1239 | SCE | ES-5275 | SCE-2801 |  | 2024-08-29 12:39 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Conductor |  | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-12161 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 2 | 372778 | 218689685 | ED-12161 | SCE | ES-5275 | SHORELINE | Other, see comment | C | Overhead | 16 |  | Marymount | Other, see comment | C | 6 | [8 empty] | 3.1127 | FALSE
33 | 7 | FIPA_2024_1010_1329 | SCE | ES-5661 | SCE-2481 |  | 2024-10-10 13:29 | 2024 | Utility staff |  | Lightning | [8 empty] | 12 | 12 | Overhead | Utility personnel |  |  |  | 1763305E-206910933 | Support Structure |  | ED-17475 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Rural | Vegetation |  | Timber fuel model |  | <0.25 | Self-extinguished |  | No |  |  | Tier 3 | 948985 | 70865521 | ED-17475 | SCE | ES-5661 | TAGGERT | Covered |  | Overhead | 12 |  | RUNNING SPRINGS | Aluminum conductor steel reinforced (ACSR) |  | 1/0 | [8 empty] | 3.3183 | FALSE
29 | 18 | FIPA_2024_1024_1529 | SCE | ES-5015 | SCE-2646 |  | 2024-10-24 15:29 | 2024 | Public |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 0 | Support Structure |  | ED-19694 | Secondary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <0.25 | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 2 | 55941 | 133940812 | ED-19694 | SCE | ES-5015 | ANGELES | Other, see comment | A | Overhead | 16 |  | GOULD | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 5.2458 | 1
32 | 11 | FIPA_2024_1106_0830 | SCE | ES-5580 | SCE-2353 |  | 2024-11-06 08:30 | 2024 | Fire agency |  | Vegetation contact | [8 empty] | 16 | 16 | Overhead | Utility personnel |  |  |  | 1584827E-201856148 | Support Structure |  | ED-08707 | Secondary Distribution Line | Weather |  | Yes | 2024-11-06 10:00 | No |  | Yes | 2024-11-06 10:00 | Urban | Vegetation |  | Fire-resistive fuel bed |  | <0.25 | Fire agency | Ventura County Fire Department | No |  |  | Tier 3 | 857453 | 303514935 | ED-08707 | SCE | ES-5580 | HOSS | Other, see comment | A | Overhead | 16 |  | ROYAL | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 77.71 | 1
31 | 15 | FIPA_2024_1109_1544 | SCE | ED-7657 | SCE-2679 |  | 2024-11-09 15:44 | 2024 | Fire agency |  | Equipment failure | [6 empty] | Connector device |  | 12 | 12 | Overhead | Utility personnel |  |  |  | 356425S-201298179 | Support Structure |  | ED-14005 | Secondary Distribution Line |  |  | No |  | No |  | No |  | Rural | Vegetation |  | Grass fuel model |  | 0.26-9.99 | Fire agency | Riverside County Fire Departme | No |  |  | Tier 3 | 821626 | 84010534 | ED-14005 | SCE | ED-7657 | PHEASANT | Covered |  | Overhead | 12 |  | PHEASANT P.T. | Aluminum conductor steel reinforced (ACSR) |  | 1/0 |  |  |  | 2021-07-20 | 2021 | 0-9 |  |  | 6.0709 | 1
30 | 6 | FIPA_2024_1201_0933 | SCE | ES-5576 | SCE-2223 |  | 2024-12-01 09:33 | 2024 | Fire agency |  | Object contact |  | Animal contact | [6 empty] | 16 | 16 | Overhead | Utility personnel |  | Other, see comment | Lightning Arrester | 0 | Support Structure |  | ED-02674 | Primary Distribution Line | External Force |  | No |  | No |  | No |  | Urban | Vegetation |  | Brush fuel model |  | <3 meters of linear travel | Fire agency | Los Angeles County Fire Depart | No |  |  | Tier 3 | 186173 | 10556305 | ED-02674 | SCE | ES-5576 | CALGROVE | Covered |  | Overhead | 16 |  | NEWHALL | Aluminum conductor steel reinforced (ACSR) |  | 336 |  |  |  | 1901-12-13 | 1901 | 100+ |  |  | 3.1676 | FALSE